## comments-resolutions-17Jun10
17Jun10 Security sub-group with representation from SG-Network - Resolutions / Notes (Ron's)
Darren asked about whether or not the Reqmts Table was complete and Ron indicated it's probably half way there in row count and that several additional release would occur up into 3rd Qtr this year for the Reqmts Table and that the SRS is targeted for completion end of year and that the SRS would include some summary of the Reqmts Table, but would direct reader to the Requirements Table e.g. the database preferably and at least the spreadsheet.
Several were not interested in SG-Network including CIA values into the Requirement Table only after vetted by OpenSG Security, or that OpenSG Security alone determine those values. Having SG-Network prepare the 1st pass at the CIA values has helped generate discussion, and that SG-Network has understood the assumptions & context of the payloads and their content which is not currently documented in the SRS. This is another reason to add the SG-Network sssumptions into the SRS, especially of payload content as that info helps drive CIA values.
Ron stressed that SG-Network was documenting "business" requirements and being tech agnostic. SG-Network had relied on the NISTIR 7628 def of the CIA values and using tables 2.2 & 3.3 of the LIC to CIA mapping as a starting point, but then went from there down to the payload level. SG-Network made no assumptions as to what security technologies or mechanisms would need to be implemented to address the CIA risk levels. Once again SG-Network was focusing on the business requirements. Ron also tried to make the point that the CIAs need to be established from that same business mind set of not taking the most restrictive, nor lest restrictive, but possiblly better/best practices for the payloads content might work well as a starting point, realizing that each utility & jurisdiction might deploy/implement with different CIAs.
If OpenSG Security wanted to take the CIAs within a payload down to specific interface or cross domain impacts, then Ron thoguht that was ok, just needs to be consistent in that treatment (that does not imply the same CIA's for all payloads that cross that interface). Darren had some concerns of going to that level as a lot of additional work on their part would be needed.
Ron agreed that comm-err Integrity carrying the same value as that payloads associated cmd (request), provided that was a best practice, not because that was the easy thing to do , but that the business requirement indicated so.
Ron did not agree (and Ron thought the group understood), that the resp-data must match the cmd(request) for the payload. All of the items depend upon the content and context of the payload. The meter read resp-data and cmd(request) example attempted to bring this out. Ron's perception was that the security reviewers were assuming the meter readings contained data that included customer account e.g. PII type of data. Ron indicated it contained a just unique identifier of that meter along with the meter data readings. This then lead into the need to make those statements in our SRS about what data is in the payloads.
Darren will work with a few of the security people to send SG-Network an email of questions they need addressed and directions to help establish the CIA assessment norms/stds for this effort.

## Reqmts-Combined
row | Rqmt Ref | Row Type (P - Parent, else null) | Data Flow Ref (min set that includes opts) - SG-Net Diag r0.5e | Data Flow from Actor | Data Flow to Actor | Use Case Ref | Requirements (assumed electric unless noted otherwise) | Payload Name - Specific Data/Mesg (Logical - info content the same) | Payload Type [cmd , ack, resp-data, comm-err, cmd-err, alarm] | Daily Clock Periods of Primary Occurance | How Often | Reliability | Latency (response time one direction) Rqmts | Candidate NIST LIC | CIA Delta Flag | Security Confidentiality (L, M, H) | Security Integrity (L, M, H) | Security Availability (L, M, H) | Payload Size Type (native, Intgrt, display) | App Payload Size - bytes | Implication (sys critical, low importance) | Chng Security Confidentiality (L, M, H) | Chng Security Integrity (L, M, H) | Chng Security Availability (L, M, H)
2 | MR- 1 | P | 1Aa | CIS/Billing - Utility | MDMS | Meter reading | CIS - Utility shall be able to send bulk meter read information requests to MDMS | bulk_Mtr-read_cmd | cmd | 6PM - 6AM | typically performed in x batches of y number meters once per day (x) * (y) = total Smart Meters deployed per named utility | > 99.5% | < 1hr | 3a |  | L | M | M | Intgrt | 25 |  | L | M | M
3 | MR- 5 | P | 1B | MDMS | AMI Head-End | Meter reading | MDMS shall be able to send bulk meter read information requests to Head End | bulk_Mtr-read_cmd | cmd | 6PM - 6AM | typically performed in x batches of y number meters once per day (x) * (y) = total Smart Meters deployed per named utility | > 99.5% | < 1hr | 3a |  | L | M | M | Intgrt | 25 |  | L | M | M
4 | MR- 6 | P | 1Aa | MDMS | CIS/Billing - Utility | Meter reading | MDMS shall be able to process & send bulk meter read information data to CIS - Utility | bulk_Mtr-read_resp-data | resp-data | 6PM - 6AM | typically performed in x batches of y number meters once per day (x) * (y) = total Smart Meters deployed per named utility | > 99.5% | < 1hr | 3a |  | M | M | M | Intgrt | xMB |  | M | M | M
5 | MR- 13 | P | 1B | AMI Head End | MDMS | Meter reading | AMI Head-End shall be able to process & forward on-demand meter read data to MDMS | bulk_Mtr-read_resp-data | resp-data | 6PM - 6AM | typically performed in x batches of y number meters once per day (x) * (y) = total Smart Meters deployed per named utility | > 99.5% | < 1hr | 3a |  | M | M | M | Intgrt | xMB |  | M | M | M
6 | MR- 36 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] | Smart Meter - Gas Com | AMI Head-End | Meter reading | Smart Meter (Gas Commercial/Industrial) shall be able to send multi interval-data meter reads data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per day per gas C/I meter. May have 15min vs 1hr interval data | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 3a, 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
7 | MR- 32 |  | 1D | Smart Meter - Gas Com | DAP | Meter reading | Smart Meter (Gas Commercial/Industrial) shall be able to send multi interval-data meter reads data to DAP | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per day per gas C/I meter. May have 15min vs 1hr interval data | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
8 | MR- 58 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to forward Smart Meter (Gas Commercial) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
9 | MR- 59 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Gas Commercial) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
10 | MR- 60 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Gas Commercial) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
11 | MR- 61 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Smart Meter (Gas Commercial) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-C/I-meter per day | > 99.5% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
12 | MR- 37 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] | Smart Meter - Gas Resdnt | AMI Head-End | Meter reading | Smart Meter (Gas Residential) shall be able to send multi interval-data meter reads data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per day per gas resdnt meter, with 4hr -24h interval data | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 3a, 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
13 | MR- 33 |  | 1D | Smart Meter - Gas Resdnt | DAP | Meter reading | Smart Meter (Gas Residential) shall be able to send multi interval-data meter reads data to DAP | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per day per gas resdnt meter, with 4hr -24h interval data | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
14 | MR-62 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to forward Smart Meter (Gas Residential) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
15 | MR-63 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Gas Residential) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
16 | MR-64 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Gas Residential) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
17 | MR-65 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Smart Meter (Gas Residential) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 trans per DAPjm-gas-resdnt-meter per day | > 99.5% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
18 | MR- 38 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] | Smart Meter - Elect C/I | AMI Head-End | Meter reading | Smart Meter (Electric Commercial/Industrial) shall be able to send multi interval-data meter reads data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 12-24 trans per day per electric C/I meter, Intervals of 15min to 1hr, 4-20 data points per interval | >98% success every 3 hours, >99.5% success over 2 days, > 99.5% over two days | < 3hr expected window of data delivery | 3a, 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
19 | MR- 34 |  | 1D | Smart Meter - Elect C/I | DAP | Meter reading | Smart Meter (Electric Commercial/Industrial) shall be able to send multi interval-data meter reads data to DAP | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 12-24 trans per day per electric C/I meter, Intervals of 15min to 1hr, 4-20 data points per interval | >98% success every 3 hours, >99.5% success over 2 days, > 99.5% over two days | < 3hr expected window of data delivery | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
20 | MR- 66 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to forward Smart Meter (Electric Commercial/Industrial) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
21 | MR- 67 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Electric Commercial/Industrial) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
22 | MR- 68 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Electric Commercial/Industrial) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-C/I-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
23 | MR- 69 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Smart Meter (Electric Commercial/Industrial) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-C/I-meter per day | > 99.5% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 1600 | Need to retry, Potential broken cash register, Not system critical | M | M | L
24 | MR- 39 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] | Smart Meter - Elect Resdnt | AMI Head-End | Meter reading | Smart Meter (Electric Residential) shall be able to send multi interval-data meter reads data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per day per electric resdnt meter, Intervals of 15min to 1hr, 4-8 data points per interval | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 3a, 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
25 | MR- 35 |  | 1D | Smart Meter - Elect Resdnt | DAP | Meter reading | Smart Meter (Electric Residential) shall be able to send multi interval-data meter reads data to DAP | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per day per electric resdnt meter, Intervals of 15min to 1hr, 4-8 data points per interval | 90% success every 4-6 hours, 98% success over a day, > 99.5% over two days | < 4hr expected window of data delivery | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
26 | MR- 26 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to forward Smart Meter (Electric Residential) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
27 | MR- 70 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Electric Residential) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
28 | MR- 71 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward Smart Meter (Electric Residential) multiple-interval-data as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-resdnt-meter per day | > 99% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
29 | MR- 72 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Smart Meter (Electric Residential) multiple-interval-data to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 trans per DAPjm-elect-resdnt-meter per day | > 99.5% | < 10s | 10a, 10b |  | M | M | L | Native or Intgrt | 1600 - 2400 | Need to retry, Potential broken cash register, Not system critical | M | M | L
30 | MR- 7 | P | 1B + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + [1D | MDMS | Smart Meter | Meter reading | MDMS may be able to send multiple interval meter reading request to Smart Meter | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99.5% | < 15s | 3a, 10a, 10b |  | M | M | L | Intgrt | 25 | May need to retry, Not system critical | M | M | L
31 | MR- 8 |  | 1B | MDMS | AMI Head-End | Meter reading | MDMS may be able to send multiple interval meter reading request to AMI Head-End | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | M | L | Intgrt | 25 | May need to retry, Not system critical | M | M | L
32 | MR- 14 |  | 1Ca | AMI Head End | DAP | Meter reading | AMI Head-End may be able to process & send/forward multiple interval meter reading request to Smart Meter via DAP | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
33 | MR- 73 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | Meter reading | Head End shall be able to process & forward multiple interval meter reading request as routed througj Internet / Extranet gateways(s) - Utility | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
34 | MR- 74 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward multiple interval meter reading request to DAP | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
35 | MR- 75 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward multiple interval meter reading request to DAP | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
36 | MR- 25 |  | 1D | DAP | Smart Meter | Meter reading | DAP may be able to forward multiple interval meter reading request to Smart Meter | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 98% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
37 | MR- 15 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + 1B | Smart Meter | MDMS | Meter reading | Smart Meter may be able to process & send/forward multiple interval meter reading data (per specific meter request from MDMS) to MDMS | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 98% | < 15s | 3a |  | M | M | L | Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
38 |  |  | 1D | Smart Meter | DAP | Meter reading | Smart Meter shall be able to send multiple interval meter reading data (per specific meter request from MDMS) to DAP | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 98% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
39 |  |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to process & forward multiple interval meter reading data (per specific meter request from MDMS) to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
40 |  |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward multiple interval meter reading data (per specific meter request from MDMS) as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
41 |  |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward multiple interval meter reading data (per specific meter request from MDMS) as routed through Internet / Extranet gateway(s) - Utility | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
42 |  |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward multiple interval meter reading data (per specific meter request from MDMS) to AMI Head-End | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 DAPjm-mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | M | L | Native or Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
43 |  |  | 1B | AMI Head End | MDMS | Meter reading | AMI Head-End shall be able to process & forward multiple interval meter reading data (per specific meter request from MDMS) to MDMS | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | M | L | Intgrt | 200 - 2400 | May need to estimate or manually read, Not system critical | M | M | L
44 | MR- 2 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | Meter reading | CIS - Utility shall be able to send on-demand meter read request to the Smart Meter via the Head-End | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 98% | < 15s | 3a, 10a, 10b, 11 |  | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | L | M | L
45 | MR- 3 |  | 1Aa | CIS/Billing - Utility | MDMS | Meter reading | CIS - Utility may be able to send on-demand meter read request to MDMS | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | L | M | L
46 | MR- 4 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | Meter reading | CIS - Utility may be able to send on-demand meter read request to AMI Head-End | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | L | M | L
47 | MR- 9 |  | 1B | MDMS | AMI Head-End | Meter reading | MDMS shall be able to process & forward on-demand meter read request to AMI Head End, as maybe received from CIS - Utility | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to retry. Not system critical | L | M | L
48 | MR- 16 |  | 1Ca | AMI Head End | DAP | Meter reading | Head End shall be able to process & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
49 | MR- 76 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | Meter reading | Head End shall be able to process & forward on-demand meter read requests as routed througj Internet / Extranet gateways(s) - Utility | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
50 | MR- 77 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
51 | MR- 78 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
52 | MR- 27 |  | 1D | DAP | Smart Meter | Meter reading | DAP shall be able to process & forward on-demand meter read requests to the Smart Meter (Electric or Gas, Residential or Commerical/Industrial) | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 DAPjm-mtrs per day | > 98% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
53 | MR- 29 | P | [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(1B + 1Aa) or 1Ab) or 1B or 7] | DAP | CIS/Billing - Utility, MDMS, NMS | Meter reading | DAP shall be able to report & send "DAP to Smart Meter on-demand meter read request communications errors", to CIS/Billing - Utility and/or MDMS and/or NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 10s | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
54 | MR- 28 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to report & send "DAP to Smart Meter on-demand meter read request communications errors", to AMI Head-End | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
55 | MR- 79 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "DAP to Smart Meter on-demand meter read request communications errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
56 | MR- 80 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "DAP to Smart Meter on-demand meter read request communications errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
57 | MR- 81 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "DAP to Smart Meter on-demand meter read request communications errors" to AMI Head-End | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
58 | MR- 17 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Meter reading | AMI Head-End may be able to report & send "on-demand meter read request communication errors to Smart Meter" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
59 | MR- 19 |  | 1B | AMI Head End | MDMS | Meter reading | AMI Head-End shall be able to report & send any "on-demand meter read request communication errors to Smart Meter" to MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
60 | MR- 10 |  | 1Aa | MDMS | CIS/Billing - Utility | Meter reading | MDMS may be able to report & send "on-demand meter read request communication errors to Smart Meter" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
61 | MR- 18 |  | 7 | AMI Head End | NMS | Meter reading | AMI Head-End shall be able to report & send "on-demand meter read request communication errors to Smart Meter" to NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
62 | MR- 54 | P | tbd | IHD | MDMS, NMS | Meter reading | IHD shall be able to report & send "IHD to Meter on-demand meter read request communications errors", to MDMS and/or NMS via comm path from IHD to meter when re-established OR alternate dataflow to NMS and/or MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 98% | tbd | tbd | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
63 | MR- 57 | P | tbd | Cust. EMS | MDMS, NMS | Meter reading | Cust. EMS shall be able to report & send "Cust. EMS to Meter on-demand meter read request communications errors", to MDMS and/or NMS via comm path from Cust. EMS to meter when re-established OR alternate dataflow to NMS and/or MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 98% | tbd | tbd | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
64 | MR- 43 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [((1B + 1Aa) or 1Ab) or 1B or 7] | Smart Meter | CIS/Billing - Utility, MDMS, NMS | Meter reading | Smart Meter shall be able to report & forward Meter on-demand read request app errors to CIS/Billing and/or MDMS and/or NMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 98% | < 15s | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
65 | MR- 42 |  | 1D | Smart Meter | DAP | Meter reading | Smart Meter shall be able to report & forward Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
66 | MR- 30 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to process & forward Meter on-demand read request app errors to AMI Head-End | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per each DAPjm-meters' app error event | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
67 | MR- 82 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "Meter on-demand read request app errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per each DAPjm-meters' app error event | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
68 | MR- 83 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "Meter on-demand read request app errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per each DAPjm-meters' app error event | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
69 | MR- 84 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "Meter on-demand read request app errors" to AMI Head-End | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per each DAPjm-meters' app error event | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
70 | MR- 20 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Meter reading | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to CIS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
71 | MR- 21 |  | 1B | AMI Head End | MDMS | Meter reading | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to MDMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
72 | MR- 11 |  | 1Aa | MDMS | CIS/Billing - Utility | Meter reading | MDMS may be able to process & forward Meter on-demand read request app errors to CIS - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
73 | MR- 22 |  | 7 | AMI Head End | NMS | Meter reading | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to NMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
74 | MR- 41 | P | 16Aa | Smart Meter | IHD | Meter reading | Smart Meter shall be able to report & send Meter on-demand read request app errors to IHD via Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 5s | 11 | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
75 | MR- 40 | P | 16Ca | Smart Meter | Cust. EMS | Meter reading | Smart Meter shall be able to report & send Meter on-demand read request app errors to Cust. EMS via Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per meter per x on-demand cmds per time period | > 99% | < 5s | 11 | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
76 | MR- 46 | P | 1D + 5Bb + 16Cb | 2-Way Meter | Cust. EMS - Utility | Meter reading | 2-Way Meter shall be able to report & send Meter on-demand read request app errors to Cust. EMS - Utility via non-Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per Cust. EMS - Utility per x on-demand cmds per time period | > 98% | < 15s | 11 | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
77 | MR-85 |  | 1D | 2-Way Meter | DAP | Meter reading | 2-Way Meter shall be able to send Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per Cust. EMS - Utility per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
78 | MR- 86 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | Meter reading | DAPshall be able to process and forward Meter on-demand read request app errors to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per Cust. EMS - Utility per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
79 | MR- 87 |  | 16Ab | ESI - non-Smart Meter - Utility | Cust. EMS - Utility | Meter reading | ESI - non-Smart Meter - Utility shall be able to process and forward Meter on-demand read request app errors to Cust. EMS - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per Cust. EMS - Utility per x on-demand cmds per time period | > 99% | < 5s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
80 | MR- 47 | P | 1D + 5Bb + 16Ab | 2-Way Meter | IHD | Meter reading | 2-Way Meter shall be able to report & send Meter on-demand read request app errors to IHD via non-Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per IHD per x on-demand cmds per time period | > 98% | < 15s | 11 | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
81 | MR- 88 |  | 1D | 2-Way Meter | DAP | Meter reading | 2-Way Meter shall be able to send Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per IHD per x on-demand cmds per time period | > 98% | < 5s | 11 |  | L | L | L | Intgrt | 100 |  | L | L | L
82 | MR- 89 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | Meter reading | DAPshall be able to process and forward Meter on-demand read request app errors to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per IHD per x on-demand cmds per time period | > 98% | < 5s | 11 |  | L | L | L | Intgrt | 100 |  | L | L | L
83 | MR- 90 |  | 16Ab | ESI - non-Smart Meter - Utility | IHD | Meter reading | ESI - non-Smart Meter - Utility shall be able to process and forward Meter on-demand read request app errors to IHD | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per IHD per x on-demand cmds per time period | > 99% | < 5s | 11 |  | L | L | L | Intgrt | 100 |  | L | L | L
84 | MR- 45 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(1B + 1Aa) or 1Ab] | Smart Meter | CIS/Billing - Utility | Meter reading | Smart Meter (Electric or Gas, Residential or Commercial/Industrial) shall be able to send on-demand meter read data to CIS - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per meter per on demand request | > 98% | < 15s | 3a, 10a, 10b |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
85 | MR- 44 |  | 1D | Smart Meter | DAP | Meter reading | Smart Meter (Electric or Gas, Residential or Commercial/Industrial) shall be able to send on-demand meter read data to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per meter per on demand request | > 98% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | M | M | L
86 | MR- 31 |  | 1Ca | DAP | AMI Head-End | Meter reading | DAP shall be able to process & forward on-demand meter read data from Smart Meter to AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | M | M | L
87 | MR- 91 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "on-demand meter read data from Smart Meter" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | M | M | L
88 | MR- 92 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Meter reading | DAP shall be able to process & forward "on-demand meter read data from Smart Meter" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | M | M | L
89 | MR- 93 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Meter reading | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "on-demand meter read data from Smart Meter" to AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | M | M | L
90 | MR- 24 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Meter reading | AMI Head-End shall be able to process & forward on-demand meter read data to CIS - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
91 | MR- 23 |  | 1B | AMI Head End | MDMS | Meter reading | AMI Head-End shall be able to process & forward on-demand meter read data to MDMS | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
92 | MR- 12 |  | 1Aa | MDMS | CIS/Billing - Utility | Meter reading | MDMS may be able to process & forward on-demand meter read data to CIS - Utility as received from AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
93 | MR- 50 | P | 16Aa | ESI - Smart Meter | IHD | Meter reading | Smart Meter ESI shall be able to send on-demand meter reading request to IHD via Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per IHD per on demand request | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
94 | MR- 51 | P | 16Ca | ESI - Smart Meter | Cust. EMS | Meter reading | Smart Meter shall be able to send on-demand meter reading request to Cust. EMS via Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per Cust. EMS per on demand request | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
95 | MR- 48 | P | 1D + 5Bb + 16Ab | 2-Way Meter | IHD | Meter reading | 2-Way Meter shall be able to send on-demand meter reading request to IHD via non Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per IHD per on demand request | > 98% | < 15s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
96 | MR- 94 |  | 1D | 2-Way Meter | DAP | Meter reading | 2-Way Meter shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 98% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
97 | MR- 95 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | Meter reading | DAPshall be able to process and forward on-demand meter reading request to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 98% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
98 | MR- 96 |  | 16Ab | ESI - non-Smart Meter - Utility | IHD | Meter reading | ESI - non-Smart Meter - Utility shall be able to process and forward on-demand meter reading request to IHD | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 99% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
99 | MR- 49 | P | 1D + 5Bb + 16Cb | 2-Way Meter | Cust. EMS - Utility | Meter reading | 2-Way Meter shall be able to send on-demand meter reading request to Cust. EMS - Utility via non Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per Cust. EMS - Utility per on demand request | > 98% | < 15s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
100 | MR- 97 |  | 1D | 2-Way Meter | DAP | Meter reading | 2-Way Meter shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 98% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
101 | MR- 98 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | Meter reading | DAPshall be able to process and forward on-demand meter reading request to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 98% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
102 | MR- 99 |  | 16Ab | ESI - non-Smart Meter - Utility | Cust. EMS - Utility | Meter reading | ESI - non-Smart Meter - Utility shall be able to process and forward on-demand meter reading request to Cust. EMS -Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 99% | < 5s | 11 | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
103 | MR- 100 | P | [16Aa or (1D + 5Bb + 16Ab)] | IHD | Smart Meter | Meter reading | IHD shall be able to send on-demand meter reading request to Smart Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with IHD | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
104 | MR- 52 |  | 16Aa | IHD | Smart Meter | Meter reading | IHD shall be able to send on-demand meter reading request to Smart Meter via Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with IHD | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
105 | MR- 53 |  | 16Ab | IHD | ESI - non-Smart Meter - Utility | Meter reading | IHD shall be able to send on-demand meter reading request to non Smart Meter ESI - Utility | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
106 | MR- 101 |  | 5Bb | ESI - non-Smart Meter - Utility | DAP | Meter reading | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
107 | MR- 102 |  | 1D | DAP | 2-Way Meter | Meter reading | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to 2Way Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with IHD | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
108 | MR- 103 | P | [16Ca + (1D + 5Bb + 16Cb)] | Cust. EMS | Smart Meter | Meter reading | Customer EMS shall be able to send on-demand meter reading request to Smart Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with Cust. EMS | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
109 | MR- 55 |  | 16Ca | Cust. EMS | Smart Meter | Meter reading | Customer EMS shall be able to send on-demand meter reading request to Smart Meter via non Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with Cust. EMS | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
110 | MR- 56 |  | 16Ab | Cust. EMS | ESI - non-Smart Meter - Utility | Meter reading | Customer EMS shall be able to send on-demand meter reading request to non Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with Cust. EMS | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
111 | MR- 104 |  | 5Bb | ESI - non-Smart Meter - Utility | DAP | Meter reading | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with Cust. EMS | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
112 | MR- 105 |  | 1D | DAP | 2-Way Meter | Meter reading | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to 2Way Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per customer with Cust. EMS | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
113 | PHEV- 1 | P | 9 + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + [(5Ba + 16Ba + 16B1) or (5Bb + 16Bb + 16B1)] | LMS | PHEV | PHEV | LMS shall be able to send charging price rates to PHEV | PHEV_price_rate_cmd | cmd |  | tbd | tbd | < 15s | 3a, 10a, 10b, 11, 14 | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
114 | PHEV- 2 |  | 9 | LMS | AMI Head-End | PHEV | LMS shall be able to send charging price rates to AMI Head-End | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99.5% | < 10s | 3a | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
115 | PHEV- 4 |  | 1Ca | AMI Head End | DAP | PHEV | AMI Head-End shall be able to send charging price rates to DAP | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 10s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
116 | PHEV- 65 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PHEV | Head End shall be able to process & forward charging price rates as routed through Internet / Extranet gateways(s) - Utility | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
117 | PHEV- 66 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward charging price rates to DAP | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
118 | PHEV- 67 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward charging price rates to DAP | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
119 | PHEV- 20 |  | 5Ba | DAP | ESI - Smart Meter | PHEV | DAP shall be able to send charging price rates to Smart Meter ESI | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per DAPjm-PHEV-meter connect per day | > 98% | < 10s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
120 | PHEV- 21 |  | 5Bb | DAP | ESI - non-Smart Meter | PHEV | DAP shall be able to send charging price rates to non-Smart Meter ESI | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per DAPjm-PHEV-meter connect per day | > 98% | < 10s | 10a, 10b | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
121 | PHEV- 33 |  | 16Bb | ESI - non-Smart Meter | EVSE / EUMD | PHEV | non-Smart Meter ESI shall be able to send charging price rates to EVSE / EUMD | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 5s | 11, 14 | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
122 | PHEV- 44 |  | 16Ba | ESI - Smart Meter | EVSE / EUMD | PHEV | Smart Meter ESI shall be able to send charging price rates to EVSE / EUMD | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 5s | 11, 14 | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
123 | PHEV- 68 |  | 16B1 | EVSE / EUMD | PHEV | PHEV | EVSE / EUMD shall be able to send charging price rates to PHEV | PHEV_price_rate_cmd | cmd |  | 1 trans per 2-4 times per PHEV-meter connect per day | > 99% | < 5s | 14 | Y | L | L | L | Display | 255 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
124 | PHEV- 35 | P | 5Bb+ [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 9 | ESI - non-Smart Meter | LMS | PHEV | non-Smart Meter ESI shall be able to process & send "Send of Price Rate (from LM) to PHEV" communication failure to LMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | 0.995 | < 15sec | 3a, 10a, 10b, 14 |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
125 | PHEV- 34 |  | 5Bb | ESI - non-Smart Meter | DAP | PHEV | non-Smart Meter ESI shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DAP | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | 0.995 | <10s | 10a, 10b, 14 |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
126 | PHEV- 22 |  | 1Ca | DAP | AMI Head-End | PHEV | DAP shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to AMI Head-End | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-non-SMtr per day | > 99% | <10s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
127 | PHEV- 69 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward "Send of Price Rate (from LM) to PHEV" communication failure as routed through Internet / Extranet gateway(s) - Utility | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-non-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
128 | PHEV- 70 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward "Send of Price Rate (from LM) to PHEV" communication failure as routed through Internet / Extranet gateway(s) - Utility | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-non-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
129 | PHEV- 71 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "Send of Price Rate (from LM) to PHEV" communication failure to AMI Head-End | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-non-SMtr per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
130 | PHEV- 5 |  | 10 | AMI Head End | DMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
131 | PHEV- 6 |  | 8 | AMI Head End | DSM | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DSM | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
132 | PHEV- 8 |  | 9 | AMI Head End | LMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to LMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
133 | PHEV- 7 |  | 7 | AMI Head End | NMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to NMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-non-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
134 | PHEV- 46 | P | 5Ba+ [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 9 | ESI - Smart Meter | LMS | PHEV | Smart Meter ESI shall be able to process & send "Send of Price Rate (from LM) to PHEV" communication failure to LMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | 0.995 | < 15sec | 3a, 10a, 10b, 14 |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
135 | PHEV- 45 |  | 5Ba | ESI - Smart Meter | DAP | PHEV | Smart Meter ESI shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DAP | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | 0.995 | <10s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
136 | PHEV- 72 |  | 1Ca | DAP | AMI Head-End | PHEV | DAP shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to AMI Head-End | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99% | <10s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
137 | PHEV- 73 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward "Send of Price Rate (from LM) to PHEV" communication failure as routed through Internet / Extranet gateway(s) - Utility | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
138 | PHEV- 74 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward "Send of Price Rate (from LM) to PHEV" communication failure as routed through Internet / Extranet gateway(s) - Utility | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
139 | PHEV- 75 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "Send of Price Rate (from LM) to PHEV" communication failure to AMI Head-End | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
140 | PHEV- 76 |  | 10 | AMI Head End | DMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
141 | PHEV- 77 |  | 8 | AMI Head End | DSM | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DSM | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
142 | PHEV- 78 |  | 9 | AMI Head End | LMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to LMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
143 | PHEV- 79 |  | 7 | AMI Head End | NMS | PHEV | AMI Head-end shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to NMS | PHEV_price_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
144 | PHEV- 9 | P | 7+ [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + [(5Ba + 16Ba + 16B1) or (5Bb + 16Bb + 16B1)] | AMI Head End | PHEV, NMS | PHEV | AMI Head-End shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to PHEV & NMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 98% | < 15sec | 10a, 10b, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
145 | PHEV- 10 |  | 7 | AMI Head End | NMS | PHEV | AMI Head-End shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to NMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
146 | PHEV- 11 |  | 1Ca | AMI Head End | DAP | PHEV | AMI Head-End shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to DAP | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
147 | PHEV- 80 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PHEV | Head End shall be able to process & forward "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure as routed through Internet / Extranet gateways(s) - Utility | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
148 | PHEV- 81 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to DAP | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
149 | PHEV- 82 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to DAP | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
150 | PHEV- 23 |  | 5Ba | DAP | ESI - Smart Meter | PHEV | DAP shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to Smart Meter ESI | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs per day | > 98% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
151 | PHEV- 24 |  | 5Bb | DAP | ESI - non-Smart Meter | PHEV | DAP shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to non-Smart Meter ESI | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs per day | > 98% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
152 | PHEV- 36 |  | 16Bb | ESI - non-Smart Meter | EVSE / EUMD | PHEV | non-Smart Meter ESI shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to EVSE / EUMD | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | <10s | 11, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
153 | PHEV- 47 |  | 16Ba | ESI - Smart Meter | EVSE / EUMD | PHEV | Smart Meter ESI shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS" communication failure to EVSE / EUMD | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | <10s | 11, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
154 | PHEV- 83 |  | 16B1 | EVSE / EUMD | PHEV | PHEV | EVSE / EUMD shall be able to send charging price rates to PHEV | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | < 5s | 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
155 | PHEV- 49 | P | [7 or 9] | AMI Head End | LMS | PHEV | AMI Head-End shall be able to process & send "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to LMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | < 10s | 10a, 10b, 14 |  | L | L | L | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
156 | PHEV- 12 |  | 7 | AMI Head End | NMS | PHEV | AMI Head-end shall be able to forward "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to NMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
157 | PHEV- 13 |  | 9 | AMI Head End | LMS | PHEV | AMI Head-end shall be able to forward "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to LMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
158 | PHEV- 25 |  | [1Ca or 1Cb] | DAP | AMI Head-End | PHEV | DAP shall be able to forward "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to AMI Head-End | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs per day | > 99% | < 5s | 10a, 10b |  |  |  |  | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate
159 | PHEV- 37 |  | 5Bb | ESI - non-Smart Meter | DAP | PHEV | non-Smart Meter ESI shall be able to forward "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to DAP | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | <10s | 10a, 10b |  |  |  |  | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate
160 | PHEV- 38 |  | 5Bb+ [1Ca or 1Cb] + 9 | ESI - non-Smart Meter | LMS | PHEV | non-Smart Meter ESI shall be able to process & send "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to LMS | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | <10s | 3a, 10a, 10b, 14 |  |  |  |  | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate
161 | PHEV- 48 |  | 5Ba | ESI - Smart Meter | DAP | PHEV | Smart Meter ESI shall be able to forward "negotiate Power Charging Rate messages (from LMS) to PHEV" communication failure to DAP | PHEV_pwr_chrg_rate_comm_err | comm-err |  | 1 trans per 1000 PHEV-mtrs per day | > 99% | <10s | 10a, 10b |  |  |  |  | Native or Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate
162 | PHEV- 3 | P | 9 + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + [(5Ba + 16Ba + 16B1) or (5Bb + 16Bb + 16B1)] | LMS | PHEV | PHEV | LMS shall be able to negotiate Power Charging Rate with PHEV | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | tbd | < 15s | 3a, 10a, 10b, 11, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
163 | PHEV- 84 |  | 9 | LMS | AMI Head-End | PHEV | LMS shall be able to process & send negotiate Power Charging Rate messages to AMI Head-End | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99.5% | < 10s | 3a |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
164 | PHEV- 15 |  | 1Ca | AMI Head End | DAP | PHEV | AMI Head-End shall be able to process & forward negotiate Power Charging Rate messages (from LMS) to DAP | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99% | < 10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
165 | PHEV- 85 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PHEV | Head End shall be able to process & forward charging price rates as routed through Internet / Extranet gateways(s) - Utility | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
166 | PHEV- 86 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward charging price rates to DAP | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
167 | PHEV- 87 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward charging price rates to DAP | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
168 | PHEV- 27 |  | 5Ba | DAP | ESI - Smart Meter | PHEV | DAP shall be able to forward negotiate Power Charging Rate messages (from LMS) to Smart Meter ESI | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | <150 trans per 1000 DAPjm-mtrs 2-4 times per day | > 98% | <10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
169 | PHEV- 28 |  | 5Bb | DAP | ESI - non-Smart Meter | PHEV | DAP shall be able to forward negotiate Power Charging Rate messages (from LMS) to non-Smart Meter ESI | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | <150 trans per 1000 DAPjm-mtrs 2-4 times per day | > 98% | <10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
170 | PHEV- 40 |  | 16Bb | ESI - non-Smart Meter | EVSE / EUMD | PHEV | non-Smart Meter ESI shall be able to forward negotiate Power Charging Rate messages (from LMS) to EVSE / EUMD | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 99% | <10s | 11, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
171 | PHEV- 51 |  | 16Ba | ESI - Smart Meter | EVSE / EUMD | PHEV | Smart Meter ESI shall be able to forward negotiate Power Charging Rate messages (from LMS) to EVSE / EUMD | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 99% | <10s | 11, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
172 | PHEV- 88 |  | 16B1 | EVSE / EUMD | PHEV | PHEV | EVSE / EUMD shall be able to send negotiate Power Charging Rate messages (from LMS) to PHEV | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 99% | < 5s | 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
173 | PHEV- 57 | P | [(16B1 + 16Ba + 5Ba) or (16B1 + 16Bb + 5Bb)] + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + 9 | PHEV | LMS | PHEV | PHEV shall be able to send negotiate Power Charging Rate messages to LMS | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | tbd | < 15s | 3a, 10a, 10b, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
174 | PHEV- 89 |  | 16B1 | PHEV | EVSE / EUMD | PHEV | EVSE / EUMD shall be able to send negotiate Power Charging Rate messages (from LMS) to EVSE / EUMD | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 99% | < 5s | 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
175 | PHEV- 55 |  | 16Ba | EVSE / EUMD | ESI - Smart Meter | PHEV | EVSE / EUMD shall be able to send negotiate Power Charging Rate messages (from PHEV) to Smart Meter ESI | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | tbd | tbd | 11, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
176 | PHEV- 56 |  | 16Bb | EVSE / EUMD | ESI - non-Smart Meter | PHEV | EVSE / EUMD shall be able to send negotiate Power Charging Rate messages (from PHEV) to non-Smart Meter ESI | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | tbd | tbd | 11, 14 |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
177 | PHEV- 39 |  | 5Bb | ESI - non-Smart Meter | DAP | PHEV | non-Smart Meter ESI shall be able to forward negotiate Power Charging Rate messages (from PHEV) to DAP | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 98% | <10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
178 | PHEV- 50 |  | 5Ba | ESI - Smart Meter | DAP | PHEV | Smart Meter ESI shall be able to forward negotiate Power Charging Rate messages (from PHEV) to DAP | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 1 thread, 2-4 trans per PHEV connected meter per day | > 98% | <10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
179 | PHEV- 26 |  | 1Ca | DAP | AMI Head-End | PHEV | DAP shall be able to forward negotiate Power Charging Rate messages (from PHEV) to AMI Head-End | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 DAPjm-mtrs 2-4 times per day | > 99% | <10s | 10a, 10b |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
180 | PHEV- 90 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
181 | PHEV- 91 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
182 | PHEV- 92 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward PHEV VIN information request to AMI Head-End | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
183 | PHEV- 14 |  | 9 | AMI Head End | LMS | PHEV | AMI Head-End shall be able to process & forward negotiate Power Charging Rate messages (from PHEV) to LMS | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd |  | 150 trans per 1000 mtrs 2-4 times per day | > 99.5% | < 10s | 3a |  | L | M | L | Intgrt | 100 | Customer Service issue, PHEV battery does not get re-charged. Potential system impact in scale | L | M | L
184 | PHEV- 18 | P | [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + [(5Ba + 16Ba + 16B1) or (5Bb + 16Bb + 16B1)] | AMI Head End | PHEV | PHEV | AMI Head-End shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to PHEV | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99.5% | < 10s | 10a, 10b, 11, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
185 | PHEV- 19 |  | 1Ca | AMI Head End | DAP | PHEV | AMI Head-End shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to DAP | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99.5% | <10s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
186 | PHEV- 93 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PHEV | Head End shall be able to process & forward "PHEV VIN information request to MDMS (from PHEV)" communications failure as routed through Internet / Extranet gateways(s) - Utility | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
187 | PHEV- 94 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "PHEV VIN information request to MDMS (from PHEV)" communications failure to DAP | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
188 | PHEV- 95 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "PHEV VIN information request to MDMS (from PHEV)" communications failure to DAP | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
189 | PHEV- 31 |  | 5Ba | DAP | ESI - Smart Meter | PHEV | DAP shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to Smart Meter ESI | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs per day | > 99% | <10s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
190 | PHEV- 32 |  | 5Bb | DAP | ESI - non-Smart Meter | PHEV | DAP shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to non-Smart Meter ESI | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per 1000 DAPjm-PHEV-mtrs per day | > 99% | <10s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
191 | PHEV- 43 |  | 16Bb | ESI - non-Smart Meter | EVSE / EUMD | PHEV | non-Smart Meter ESI shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to EVSE / EUMD | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 98% | <10s | 11, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
192 | PHEV- 54 |  | 16Ba | ESI - Smart Meter | EVSE / EUMD | PHEV | Smart Meter ESI shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to EVSE / EUMD | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 98% | <10s | 11, 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
193 | PHEV- 96 |  | 16B1 | EVSE / EUMD | PHEV | PHEV | EVSE / EUMD shall be able to send charging price rates to PHEV | PHEV_Vin_data_comm_err | comm-err |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 5s | 14 |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
194 | PHEV- 60 | P | [(16B1 + 16Ba + 5Ba) or (16B1 + 16Bb + 5Bb)] + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + 9 | PHEV | LMS | PHEV | PHEV shall be able to process & send charging status of the PHEV to LMS | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | tbd | < 15s | 3a, 10a, 10b, 11, 14 |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
195 | PHEV- 97 |  | 16B1 | PHEV | EVSE / EUMD | PHEV | PHEV shall be able to send PHEV VIN information request to EVSE / EUMD | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | > 99% | < 5s | 14 |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
196 | PHEV- 58 |  | 16Ba | EVSE / EUMD | ESI - Smart Meter | PHEV | EVSE / EUMD shall be able to process & send charging status of the PHEV to Smart Meter ESI | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | > 99% | < 10s | 11, 14 |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
197 | PHEV- 59 |  | 16Bb | EVSE / EUMD | ESI - non-Smart Meter | PHEV | EVSE / EUMD shall be able to process & send charging status of the PHEV to non-Smart Meter ESI | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | > 99% | < 10s | 11, 14 |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
198 | PHEV- 52 |  | 5Ba | ESI - Smart Meter | DAP | PHEV | Smart Meter ESI shall be able to forward charging status of the PHEV to DAP | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | > 98% | < 10s | 10a, 10b |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
199 | PHEV- 41 |  | 5Bb | ESI - non-Smart Meter | DAP | PHEV | non-Smart Meter ESI shall be able to forward charging status of the PHEV to DAP | PHEV_pwr_chrg_status_resp-data | resp-data |  | 2-4 trans per PHEV charging event per day | > 98% | < 10s | 10a, 10b |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
200 | PHEV- 29 |  | 1Ca | DAP | AMI Head-End | PHEV | DAP shall be able to forward charging status of the PHEV to AMI Head-end | PHEV_pwr_chrg_status_resp-data | resp-data |  | 150 trans per 1000 DAPlm-PHEV-mtrs 2-4 times per day | > 99% | < 10s | 10a, 10b |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
201 | PHEV- 98 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_pwr_chrg_status_resp-data | resp-data |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
202 | PHEV- 99 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_pwr_chrg_status_resp-data | resp-data |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
203 | PHEV- 100 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward PHEV VIN information request to AMI Head-End | PHEV_pwr_chrg_status_resp-data | resp-data |  | 150 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr 2-4 times per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
204 | PHEV- 16 |  | 9 | AMI Head End | LMS | PHEV | AMI Head-End shall be able to forward charging status of the PHEV to LMS | PHEV_pwr_chrg_status_resp-data | resp-data |  | 150 trans per 1000 PHEV-mtrs 2-4 times per day | > 99.5% | < 10s | 3a |  | L | L | L | Intgrt | 100 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | L | L
205 | PHEV-64 | P | [(16B1 + 16Ba + 5Ba) or (16B1 + 16Bb + 5Bb)] + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + 1B | PHEV | MDMS | PHEV | PHEV shall be able to publish PHEV VIN information request to MDMS | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 98% | < 15s | 3a, 10a, 10b, 11, 14 |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
206 | PHEV- 101 |  | 16B1 | PHEV | EVSE / EUMD | PHEV | PHEV shall be able to send PHEV VIN information request to EVSE / EUMD | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 5s | 14 |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
207 | PHEV- 62 |  | 16Bb | EVSE / EUMD | ESI - non-Smart Meter | PHEV | EVSE / EUMD shall be able to process & send PHEV VIN information request to non-Smart Meter ESI | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 10s | 11, 14 |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
208 | PHEV- 61 |  | 16Ba | EVSE / EUMD | ESI - Smart Meter | PHEV | EVSE / EUMD shall be able to process & send PHEV VIN information request to Smart Meter ESI | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 10s | 11, 14 |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
209 | PHEV- 53 |  | 5Ba | ESI - Smart Meter | DAP | PHEV | Smart Meter ESI shall be able to forward PHEV VIN information request to DAP | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 98% | < 10s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
210 | PHEV- 42 |  | 5Bb | ESI - non-Smart Meter | DAP | PHEV | non-Smart Meter ESI shall be able to forward PHEV VIN information request to DAP | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 98% | < 10s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
211 | PHEV- 30 |  | 1Ca | DAP | AMI Head-End | PHEV | DAP shall be able to forward PHEV VIN information request to AMI Head-End | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
212 | PHEV- 102 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_Vin_data_cmd | cmd |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
213 | PHEV- 103 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PHEV | DAP shall be able to process & forward PHEV VIN information request as routed through Internet / Extranet gateway(s) - Utility | PHEV_Vin_data_cmd | cmd |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
214 | PHEV- 104 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | PHEV | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward PHEV VIN information request to AMI Head-End | PHEV_Vin_data_cmd | cmd |  | 1 trans per 1000 DAPjm-PHEV-mtrs-ESI-SMtr per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
215 | PHEV- 17 |  | 1B | AMI Head End | MDMS | PHEV | AMI Head-End shall be able to forward PHEV VIN information request to MDMS | PHEV_Vin_data_cmd | cmd |  | 1 trans per PHEV-mtrs connect per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 | May need to retry, system critical in scale, PHEV could charge at minimum rate | L | M | L
216 | SS- 1 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | Service Switch | CIS - Utility shall be able to send a scheduled cancel service switch operate request to Smart Meter | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 98% | < 1m | 3a, 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
217 | SS- 2 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | Service Switch | CIS - Utility shall be able to send a scheduled cancel service switch operate request to AMI Head-End | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
218 | SS- 43 |  | 1Aa | CIS/Billing - Utility | MDMS | Service Switch | CIS - Utility shall be able to send a scheduled cancel service switch operate request to MDMS | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
219 | SS- 7 |  | 1B | MDMS | AMI Head-End | Service Switch | MDMS shall be able to process & forward a scheduled cancel service switch operate request to AMI Head-End, as maybe received from CIS - Utility | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
220 | SS- 10 |  | 1Ca | AMI Head End | DAP | Service Switch | AMI Head-End shall be able to process & forward a scheduled cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
221 |  |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | Service Switch | Head End shall be able to process & forward a scheduled cancel service switch operate request as routed througj Internet / Extranet gateways(s) - Utility | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
222 |  |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a scheduled cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
223 |  |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a scheduled cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
224 | SS- 26 |  | 1D | DAP | Smart Meter | Service Switch | DAP shall be able to forward a scheduled cancel service switch operate request to Smart Meter | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
225 | SS- 3 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | Service Switch | CIS - Utility shall be able to send a service switch operate request to Smart Meter | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 98% | < 1m | 3a, 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
226 | SS- 4 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | Service Switch | CIS - Utility shall be able to send a service switch operate request to AMI Head-End | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
227 | SS- 44 |  | 1Aa | CIS/Billing - Utility | MDMS | Service Switch | CIS - Utility shall be able to send a service switch operate request to MDMS | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
228 | SS- 8 |  | 1B | MDMS | AMI Head-End | Service Switch | MDMS shall be able to process & forward a service switch operate request to AMI Head-End, as maybe received from CIS - Utility | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
229 | SS- 11 |  | 1Ca | AMI Head End | DAP | Service Switch | AMI Head-End shall be able to process & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
230 | SS- 45 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | Service Switch | Head End shall be able to process & forward a service switch operate request as routed througj Internet / Extranet gateways(s) - Utility | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
231 | SS- 46 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
232 | SS- 47 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
233 | SS- 27 |  | 1D | DAP | Smart Meter | Service Switch | DAP shall be able to forward a service switch operate request to Smart Meter | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
234 | SS- 5 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | Service Switch | CIS - Utility shall be able to send a service switch state request to Smart Meter | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 98% | < 1m | 3a, 10a, 10b |  | L | L | L | Intgrt | 25 |  | L | L | L
235 | SS- 6 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | Service Switch | CIS - Utility shall be able to send a service switch state request to AMI Head-End | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
236 | SS- 48 |  | 1Aa | CIS/Billing - Utility | MDMS | Service Switch | CIS - Utility shall be able to send a service switch state request to MDMS | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
237 | SS- 9 |  | 1B | MDMS | AMI Head-End | Service Switch | MDMS shall be able to process & forward a service switch state request to AMI Head-End, as maybe received from CIS - Utility | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
238 | SS- 21 |  | 1Ca | AMI Head End | DAP | Service Switch | AMI Head-End shall be able to process & forward a service switch state request to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 1m | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
239 | SS- 49 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | Service Switch | Head End shall be able to process & forward a service switch state request as routed througj Internet / Extranet gateways(s) - Utility | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
240 | SS- 50 |  | 1Cb | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch state request to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
241 | SS- 51 |  | 1Cc | Internet . Extranet gateway(s) - Utility | DAP | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch state request to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | M | L
242 | SS- 33 |  | 1D | DAP | Smart Meter | Service Switch | DAP shall be able to process & forward a service switch state request to Smart Meter | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | M | L
243 | SS- 30 | P | [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [((1B + 1Aa) or 1Ab) or 1B or 7] | DAP | CIS/Billing - Utility, MDMS, NMS | Service Switch | DAP shall be able to process & send "service switch operate request (from CIS, or MDMS) communications failure" with Smart Meter, to CIS/Billing - Utility and/or MDMS and NMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99% | < 1m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
244 | SS- 29 |  | 1Ca | DAP | AMI Head-End | Service Switch | DAP shall be able to process & send "service switch operate request (from CIS, or MDMS) communications failure" with Smart Meter, to AMI Head-End | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99% | < 10s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
245 | SS- 52 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward "service switch operate request (from CIS, or MDMS) communications failure" with Smart Meter, as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 DAPjm-mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
246 | SS- 53 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward "service switch operate request (from CIS, or MDMS) communications failure" with Smart Meter, as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
247 | SS- 54 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "service switch operate request (from CIS, or MDMS) communications failure" with Smart Meter, to AMI Head-End | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
248 | SS- 16 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Service Switch | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
249 | SS- 15 |  | 1B | AMI Head End | MDMS | Service Switch | AMI Head-End shall be able to process & send "service switch operate request (from MDMS) communications failure" with Smart Meter, to MDMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
250 | SS- 55 |  | 1Aa | MDMS | CIS/Billing - Utility | Service Switch | MDMS shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
251 | SS- 14 |  | 7 | AMI Head End | NMS | Service Switch | AMI Head-End shall be able to process & send "service switch operate request (from CIS or MDMS) communications failure" with Smart Meter, to NMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
252 | SS- 42 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [8 or 9 or 1B or (1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS, LMS, DSM | Service Switch | Smart Meter shall be able to send service switch state data to CIS - Utility, MDMS, LMS, DSM | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1 trans per 1000 mtrs per day | > 98% | < 3m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
253 | SS- 41 |  | 1D | Smart Meter | DAP | Service Switch | Smart Meter shall be able to send service switch state data to DAP | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
254 | SS- 34 |  | 1Ca | DAP | AMI Head-End | Service Switch | DAP shall be able to process & forward service switch state data to AMI Head-End | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
255 | SS- 56 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch state data as routed through Internet / Extranet gateway(s) - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
256 | SS- 57 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch state data as routed through Internet / Extranet gateway(s) - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
257 | SS- 58 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch state data to AMI Head-End | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 DAPjm-mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
258 | SS- 22 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Service Switch | AMI Head-End shall be able to process & foward service switch state data to CIS - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
259 | SS- 23 |  | 1B | AMI Head End | MDMS | Service Switch | AMI Head-End shall be able to process & forward service switch state data to MDMS | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
260 | SS- 59 |  | 1Aa | MDMS | CIS/Billing - Utility | Service Switch | MDMSshall be able to process & forward service switch state data to CIS - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
261 | SS- 24 |  | 8 | AMI Head End | DSM | Service Switch | AMI Head-End shall be able to process & forward service switch state data to DSM | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
262 | SS- 25 |  | 9 | AMI Head End | LMS | Service Switch | AMI Head-End shall be able to process & forward service switch state data to LMS | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
263 | SS- 36 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | Service Switch | Smart Meter shall be able to send service switch operate acknowledgment to CIS - Utility, MDMS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 98% | < 3m | 3a, 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
264 | SS- 35 |  | 1D | Smart Meter | DAP | Service Switch | Smart Meter shall be able to send service switch operate acknowledgment to DAP | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 98% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
265 | SS- 28 |  | 1Ca | DAP | AMI Head-End | Service Switch | DAP shall be able to process & forward service switch operate acknowledgment to AMI Head-End | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99% | < 30s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
266 | SS- 60 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch operate acknowledgment as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
267 | SS- 61 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch operate acknowledgment as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
268 | SS- 62 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch operate acknowledgment to AMI Head-End | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 25 |  | L | L | L
269 | SS- 12 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Service Switch | AMI Head-End shall be able to process & forward service switch operate acknowledgment to CIS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
270 | SS- 13 |  | 1B | AMI Head End | MDMS | Service Switch | AMI Head-End shall be able to process & forward service switch operate acknowledgment to MDMS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
271 | SS- 63 |  | 1Aa | MDMS | CIS/Billing - Utility | Service Switch | MDMS shall be able to process & forward service switch operate acknowledgment to CIS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 25 |  | L | L | L
272 | SS- 38 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | Service Switch | Smart Meter shall be able to send service switch operate faillure to CIS - Utility, MDMS | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 98% | < 3m | 3a, 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
273 | SS- 37 |  | 1D | Smart Meter | DAP | Service Switch | Smart Meter shall be able to send service switch operate faillure to DAP | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 98% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
274 | SS- 31 |  | 1Ca | DAP | AMI Head-End | Service Switch | DAP shall be able to process & forward service switch operate operate faillure to AMI Head-End | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 99% | < 30s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
275 | SS- 64 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch operate operate faillure as routed through Internet / Extranet gateway(s) - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 DAPjm-mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
276 | SS- 65 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward service switch operate operate faillure as routed through Internet / Extranet gateway(s) - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 DAPjm-mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
277 | SS- 66 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch operate operate faillure to AMI Head-End | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 DAPjm-mtrs-SW-oper per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
278 | SS- 17 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Service Switch | AMI Head-End shall be able to process & forward service switch operate failure to CIS - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
279 | SS- 18 |  | 1B | AMI Head End | MDMS | Service Switch | AMI Head-End shall be able to process & forward service switch operate failure to MDMS | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
280 | SS- 67 |  | 1Aa | MDMS | CIS/Billing - Utility | Service Switch | MDMS shall be able to process & forward service switch operate failure to CIS - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per mtr per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
281 | SS- 40 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | Service Switch | Smart Meter shall be able to report & send metrology information after a successful service switch operate to CIS - Utility, MDMS | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 98% | < 1m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
282 | SS- 39 |  | 1D | Smart Meter | DAP | Service Switch | Smart Meter shall be able to report & send metrology information after a successful service switch operate to DAP | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
283 | SS- 32 |  | 1Ca | DAP | AMI Head-End | Service Switch | DAP shall be able to process & forward metrology information after a successful service switch operate to AMI Head-End | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
284 | SS- 68 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward metrology information after a successful service switch operate as routed through Internet / Extranet gateway(s) - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
285 | SS- 69 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | Service Switch | DAP shall be able to process & forward metrology information after a successful service switch operate as routed through Internet / Extranet gateway(s) - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
286 | SS- 70 |  | 1Cba | Internet . Extranet gateway(s) - Utility | AMI Head End | Service Switch | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward metrology information after a successful service switch operate to AMI Head-End | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 DAPjm-mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | M | L
287 | SS- 19 |  | 1Ab | AMI Head End | CIS/Billing - Utility | Service Switch | AMI Head-End shall be able to process & foward metrology information after a successful service switch operate to CIS - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
288 | SS- 20 |  | 1B | AMI Head End | MDMS | Service Switch | AMI Head-End shall be able to process & forward metrology information after a successful service switch operate to MDMS | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
289 | SS- 71 |  | 1Aa | MDMS | CIS/Billing - Utility | Service Switch | MDMS shall be able to process & forward metrology information after a successful service switch operate to CIS - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
290 | PP-001 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | PrePay | CIS - Utility shall be able to send a meter config for prepay capability request to Smart Meter | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 98% | < 1m | 3a, 10a, 10b |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
291 | PP-002 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utility shall be able to send a meter config for prepay capability request to MDMS | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99.5% | < 5s | 3a |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
292 | PP-003 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility shall be able to send a meter reconfig request for C12.19 prepay tables directive to AMI Head-End | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99.5% | < 5s | 3a |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
293 | PP-004 |  | B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward a meter config for prepay capability request to AMI Head-End | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99.5% | < 5s | 3a |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
294 | PP-005 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward a meter config for prepay capability request to DAP | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99% | < 5s | 10a, 10b |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
295 | PP-006 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward a meter config for prepay capability request as routed througj Internet / Extranet gateways(s) - Utility | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99.5% | < 5s | 10a, 10b |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
296 | PP-007 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a meter config for prepay capability request to DAP | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99% | < 5s | 10a, 10b |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
297 | PP-008 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a meter config for prepay capability request to DAP | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 99% | < 5s | 10a, 10b |  | L | H | L | Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
298 | PP-009 |  | 1D | DAP | Smart Meter | PrePay | DAP shall be able to process & forward a meter config for prepay capability request to Smart Meter | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 trans per prepay enrollment per premise meter | > 98% | < 5s | 10a, 10b |  | L | H | L | Native or Intgrt | 25 | Need to retry, Potential broken PrePay meter config, Not system critical | L | H | L
299 | PP-010 | P | 2Dc + [(2Ga + 2Fa + 2Da) or (2Wc + 2Wa + 2Da)] | Cust. Browser - Premise | CIS / Billing - Utility | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
300 | PP-011 |  | 2Dc + 2Ga | Cust. Browser - Premise | Internet / Extranet gateway(s) - Utility | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
301 | PP-012 |  | 2Dc + 2Wc | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer to Common Web Portal | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
302 | PP-013 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
303 | PP-014 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to Web Portal - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
304 | PP-015 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | PrePay | Web Portal - Utility shall be able to process & send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
305 | PP-016 |  | 2Da | Internet / Extranet gateway(s) - Utility | CIS / Billing - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
306 | PP-017 | P | 2Dc + [(2Gb + 2Fb + 2Db) or (2Wc + 2Wb + 2Db)] | Cust. Browser - Premise | CIS / Billing - REP | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer to CIS / Billing - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
307 | PP-018 |  | 2Dc + 2Gb | Cust. Browser - Premise | Internet / Extranet gateway(s) - REP | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
308 | PP-019 |  | 2Dc + 2Wc | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Premise shall be able to send Customer prepay enrollment requests from authenticated Customer to Common Web Portal | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
309 | PP-020 |  | 2Wb | Common Web Portal | Internet / Extranet gateway(s) - REP | PrePay | Common Web Portal shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
310 | PP-021 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to Web Portal - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
311 | PP-022 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | PrePay | Web Portal - REP shall be able to process & send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
312 | PP-023 |  | 2Db | Internet / Extranet gateway(s) - REP | CIS / Billing - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to CIS / Billing - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
313 | PP-024 | P | [(3Aa + 2Fa + 2Da) or (2Wd + 2Wa +2Da)] | Cust. Browser - Mobile | CIS / Billing - Utility | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay enrollment per premise meter | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
314 | PP-025 |  | 3Aa | Cust. Browser - Mobile | Internet / Extranet gateway(s) - Utility | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
315 | PP-026 |  | 2Wd | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer to Common Web Portal | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
316 | PP-027 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
317 | PP-028 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to Web Portal - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
318 | PP-029 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | PrePay | Web Portal - Utility shall be able to process & send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
319 | PP-030 |  | 2Da | Internet / Extranet gateway(s) - Utility | CIS / Billing - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
320 | PP-031 | P | [(3Ab + 2Fb + 2Db) or (2Wd + 2Wb +2Db)] | Cust. Browser - Mobile | CIS / Billing - REP | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer to CIS / Billing - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay enrollment per premise meter | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
321 | PP-032 |  | 3Ab | Cust. Browser - Mobile | Internet / Extranet gateway(s) - REP | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
322 | PP-033 |  | 2Wd | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Mobile shall be able to send Customer prepay enrollment requests from authenticated Customer to Common Web Portal | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
323 | PP-034 |  | 2Wb | Common Web Portal | Internet / Extranet gateway(s) - REP | PrePay | Common Web Portal shall be able to send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay enrollment per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
324 | PP-035 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to Web Portal - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
325 | PP-036 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | PrePay | Web Portal - REP shall be able to process & send Customer prepay enrollment requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
326 | PP-037 |  | 2Db | Internet / Extranet gateway(s) - REP | CIS / Billing - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay enrollment requests from authenticated Customer to CIS / Billing - REP | prepay_cust_enroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay enrollment per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
327 | PP-038 | P | 2Dc + [(2Ga + 2Fa + 2Da) or (2Wc + 2Wa + 2Da)] | Cust. Browser - Premise | CIS / Billing - Utility | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
328 | PP-039 |  | 2Dc + 2Ga | Cust. Browser - Premise | Internet / Extranet gateway(s) - Utility | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
329 | PP-040 |  | 2Dc + 2Wc | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer to Common Web Portal | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
330 | PP-041 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
331 | PP-042 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to Web Portal - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
332 | PP-043 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | PrePay | Web Portal - Utility shall be able to process & send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
333 | PP-044 |  | 2Da | Internet / Extranet gateway(s) - Utility | CIS / Billing - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
334 | PP-045 | P | 2Dc + [(2Gb + 2Fb + 2Db) or (2Wc + 2Wb + 2Db)] | Cust. Browser - Premise | CIS / Billing - REP | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer to CIS / Billing - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
335 | PP-046 |  | 2Dc + 2Gb | Cust. Browser - Premise | Internet / Extranet gateway(s) - REP | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
336 | PP-047 |  | 2Dc + 2Wc | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Premise shall be able to send Customer prepay unenroll requests from authenticated Customer to Common Web Portal | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
337 | PP-048 |  | 2Wb | Common Web Portal | Internet / Extranet gateway(s) - REP | PrePay | Common Web Portal shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
338 | PP-049 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to Web Portal - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
339 | PP-050 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | PrePay | Web Portal - REP shall be able to process & send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
340 | PP-051 |  | 2Db | Internet / Extranet gateway(s) - REP | CIS / Billing - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to CIS / Billing - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
341 | PP-052 | P | [(3Aa + 2Fa + 2Da) or (2Wd + 2Wa +2Da)] | Cust. Browser - Mobile | CIS / Billing - Utility | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay unenroll per premise meter | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
342 | PP-053 |  | 3Aa | Cust. Browser - Mobile | Internet / Extranet gateway(s) - Utility | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
343 | PP-054 |  | 2Wd | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer to Common Web Portal | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
344 | PP-055 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
345 | PP-056 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to Web Portal - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
346 | PP-057 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | PrePay | Web Portal - Utility shall be able to process & send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
347 | PP-058 |  | 2Da | Internet / Extranet gateway(s) - Utility | CIS / Billing - Utility | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to CIS / Billing - Utility | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per Utility Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
348 | PP-059 | P | [(3Ab + 2Fb + 2Db) or (2Wd + 2Wb +2Db)] | Cust. Browser - Mobile | CIS / Billing - REP | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer to CIS / Billing - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay unenroll per premise meter | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
349 | PP-060 |  | 3Ab | Cust. Browser - Mobile | Internet / Extranet gateway(s) - REP | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
350 | PP-061 |  | 2Wd | Cust. Browser - Premise | Common Web Portal | PrePay | Customer Browser - Mobile shall be able to send Customer prepay unenroll requests from authenticated Customer to Common Web Portal | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
351 | PP-062 |  | 2Wb | Common Web Portal | Internet / Extranet gateway(s) - REP | PrePay | Common Web Portal shall be able to send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust premise browser users prepay unenroll per premise meter | > 99% | < 10s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
352 | PP-063 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to Web Portal - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
353 | PP-064 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | PrePay | Web Portal - REP shall be able to process & send Customer prepay unenroll requests from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
354 | PP-065 |  | 2Db | Internet / Extranet gateway(s) - REP | CIS / Billing - REP | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer prepay unenroll requests from authenticated Customer to CIS / Billing - REP | prepay_cust_unenroll_cmd | cmd | 7AM - 10PM | 1 trans per REP Cust mobile browser users prepay unenroll per premise meter | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
355 | PP-066 | P | [1AA or 1Ab] + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(5Ba + 16Aa) or (5Bb + 16Ab)] | CIS/Billing - Utility | IHD | PrePay | CIS - Utility shall be able to send any of the PrePay messages (~10 different types) to IHD | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 30s | 3a, 10a, 10b, 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
356 | PP-067 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utilitymay be able to send any of the PrePay messages (~10 different types) to MDMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
357 | PP-068 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility may be able to send any of the PrePay messages (~10 different types) to AMI Head-End | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
358 | PP-069 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward any of the PrePay messages (~10 different types) to AMI Head End, as maybe received from CIS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
359 | PP-070 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
360 | PP-071 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward any of the PrePay messages (~10 different types) as routed through Internet / Extranet gateways(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
361 | PP-072 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
362 | PP-073 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
363 | PP-074 |  | 5Ba | DAP | ESI - Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
364 | PP-075 |  | 16Aa | ESI - Smart Meter | IHD | PrePay | ESI - Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the IHD | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
365 | PP-076 |  | 5Bb | DAP | ESI - non-Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
366 | PP-077 |  | 16Aa | ESI - non-Smart Meter | IHD | PrePay | ESI - ono-Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the IHD | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99 | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
367 | PP-078 | P | [1AA or 1Ab] + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(5Ba + 16Ca) or (5Bb + 16Cb)] | CIS/Billing - Utility | Cust. EMS | PrePay | CIS - Utility shall be able to send any of the PrePay messages (~10 different types) to Cust. EMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 30s | 3a, 10a, 10b, 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
368 | PP-079 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utilitymay be able to send any of the PrePay messages (~10 different types) to MDMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
369 | PP-080 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility may be able to send any of the PrePay messages (~10 different types) to AMI Head-End | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
370 | PP-081 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward any of the PrePay messages (~10 different types) to AMI Head End, as maybe received from CIS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
371 | PP-082 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
372 | PP-083 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward any of the PrePay messages (~10 different types) as routed through Internet / Extranet gateways(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
373 | PP-084 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
374 | PP-085 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
375 | PP-086 |  | 5Ba | DAP | ESI - Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
376 | PP-087 |  | 16Ca | ESI - Smart Meter | Cust. EMS | PrePay | ESI - Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the Cust. EMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
377 | PP-088 |  | 5Bb | DAP | ESI - non-Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
378 | PP-089 |  | 16Cb | ESI - non-Smart Meter | Cust. EMS | PrePay | ESI - ono-Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the Cust. EMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99 | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
379 | PP-090 | P | [(2Db + 2Wb + 2Wa + 1cba + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(5Ba + 16Aa) or (5Bb + 16Ab)]) or (2db + 2Gb + 5Bc + 16Ab)] | CIS/Billing - REP | IHD | PrePay | CIS - REP shall be able to send any of the PrePay messages (~10 different types) to IHD via [Common Web Portal - Utility or ESI - non-Smart Meter) | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 30s | 3a, 3b, 10a, 10b, 11, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
380 | PP-091 |  | 2Db | CIS/Billing - REP | Internet / Extranet gateway(s) - REP | PrePay | CIS - REP shall be able to process & send any one of the PrePay messages (~10 different types) as routed through Internet / Extranet gateway(s) - REP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
381 | PP-092 |  | 2Wb | Internet / Extranet gateway(s) - REP | Common Web Portal | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward any one of the PrePay messages (~10 different types) to Common Web Portal | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
382 | PP-093 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to process & send any one of the PrePay messages (~10 different types) as routed through Internet / Extranet gateway(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 3b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
383 | PP-094 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head-End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any one of the PrePay messages (~10 different types) to AMI Head-End | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 3b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
384 | PP-095 |  | 2Wc + 5Bc | Common Web Portal | ESI - non-Smart Meter | PrePay | Common Web Portal shall be able to process & send any one of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
385 | PP-096 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
386 | PP-097 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward any of the PrePay messages (~10 different types) as routed through Internet / Extranet gateways(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
387 | PP-098 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
388 | PP-099 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
389 | PP-100 |  | 5Ba | DAP | ESI - Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
390 | PP-101 |  | 16Aa | ESI - Smart Meter | IHD | PrePay | ESI - Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the IHD | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99% | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
391 | PP-102 |  | 5Bb | DAP | ESI - non-Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
392 | PP-103 |  | 16Ab | ESI - non-Smart Meter | IHD | PrePay | ESI - ono-Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the IHD | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with IHD per month | > 99 | < 5s | 11, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
393 | PP-104 | P | [(2Db + 2Wb + 2Wa + 1cba + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(5Ba + 16Ca) or (5Bb + 16Cb)) or (2db + 2Gb + 5Bc + 16Cb)] | CIS/Billing - REP | Cust. EMS | PrePay | CIS - REP shall be able to send any of the PrePay messages (~10 different types) to Cust. EMS via [Common Web Portal - Utility or ESI - non-Smart Meter) | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 30s | 3a, 3b, 10a, 10b, 11, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
394 | PP-105 |  | 2Db | CIS/Billing - REP | Internet / Extranet gateway(s) - REP | PrePay | CIS - REP shall be able to process & send any one of the PrePay messages (~10 different types) as routed through Internet / Extranet gateway(s) - REP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
395 | PP-106 |  | 2Wb | Internet / Extranet gateway(s) - REP | Common Web Portal | PrePay | Internet / Extranet gateway(s) - REP shall be able to inspect & forward any one of the PrePay messages (~10 different types) to Common Web Portal | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3a |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
396 | PP-107 |  | 2Wa | Common Web Portal | Internet / Extranet gateway(s) - Utility | PrePay | Common Web Portal shall be able to process & send any one of the PrePay messages (~10 different types) as routed through Internet / Extranet gateway(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 3b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
397 | PP-108 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head-End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any one of the PrePay messages (~10 different types) to AMI Head-End | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 3b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
398 | PP-109 |  | 2Wc + 5Bc | Common Web Portal | ESI - non-Smart Meter | PrePay | Common Web Portal shall be able to process & send any one of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
399 | PP-110 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
400 | PP-111 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward any of the PrePay messages (~10 different types) as routed through Internet / Extranet gateways(s) - Utility | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
401 | PP-112 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
402 | PP-113 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward any of the PrePay messages (~10 different types) to DAP | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
403 | PP-114 |  | 5Ba | DAP | ESI - Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
404 | PP-115 |  | 16Ca | ESI - Smart Meter | Cust. EMS | PrePay | ESI - Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the Cust. EMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99% | < 5s | 11 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
405 | PP-116 |  | 5Bb | DAP | ESI - non-Smart Meter | PrePay | DAP shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - non-Smart Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per month per DAPjm-PrePay mtr | > 98% | < 5s | 10a, 10b, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
406 | PP-117 |  | 16Cb | ESI - non-Smart Meter | Cust. EMS | PrePay | ESI - ono-Smart Meter shall be able to process & forward any of the PrePay messages (~10 different types) to the Cust. EMS | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 trans per PrePay mtr with Cust. EMS per month | > 99 | < 5s | 11, 12 |  | M | H | M | Native or Intgrt | 50 - 150 | May need to retry, Not system critical | M | H | M
407 | PP-118 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | PrePay | CIS - Utility shall be able to send a cancel of scheduled service switch operate request to Smart Meter | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
408 | PP-119 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utility shall be able to send a cancel service switch operate request to MDMS | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
409 | PP-120 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility shall be able to send a cancel service switch operate request to AMI Head-End | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
410 | PP-121 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward a cancel service switch operate request to AMI Head-End, as maybe received from CIS | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
411 | PP-122 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward a cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
412 | PP-123 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward a cancel service switch operate request as routed through Internet / Extranet gateways(s) - Utility | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
413 | PP-124 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
414 | PP-125 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a cancel service switch operate request to DAP | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
415 | PP-126 |  | 1D | DAP | Smart Meter | PrePay | DAP shall be able to process & forward a cancel service switch operate request to Smart Meter | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 trans per 1000 DAPjm-PrePay mtrs per day | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
416 | PP-127 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | PrePay | CIS - Utility shall be able to send a service switch operate request to Smart Meter | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
417 | PP-128 |  | [(1Aa + 1B) or 1Ab] | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility shall be able to send a service switch operate request to AMI Head-End | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
418 | PP-129 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utility shall be able to send a service switch operate request to MDMS | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
419 | PP-130 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility shall be able to send a service switch operate request to AMI Head-End | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
420 | PP-131 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward a service switch operate request to AMI Head-End, as maybe received from CIS | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | M | H | M | Intgrt | 25 |  | M | H | M
421 | PP-132 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Intgrt | 25 |  | M | H | M
422 | PP-133 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward a service switch operate request as routed through Internet / Extranet gateways(s) - Utility | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
423 | PP-134 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
424 | PP-135 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch operate request to DAP | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
425 | PP-136 |  | 1D | DAP | Smart Meter | PrePay | DAP shall be able to process & forward a service switch operate request to Smart Meter | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 DAPjm-PrePay mtrs per day | > 98% | < 5s | 10a, 10b |  | M | H | M | Native or Intgrt | 25 |  | M | H | M
426 | PP-137 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | PrePay | CIS - Utility shall be able to send a service switch state request to Smart Meter | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
427 | PP-138 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utility shall be able to send a service switch state request to MDMS | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
428 | PP-139 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility shall be able to send a service switch state request to AMI Head-End | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
429 | PP-140 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward a service switch state request to AMI Head-End, as maybe received from CIS - Utility | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
430 | PP-141 |  | 1Ca | AMI Head End | DAP | PrePay | AMI Head-End shall be able to process & forward a service switch state request to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 1m | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
431 | PP-142 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch state requestt to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 1m | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
432 | PP-143 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward a service switch state requestt to DAP | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 1m | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
433 | PP-144 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward a service switch state request as routed through Internet / Extranet gateways(s) - Utility | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 1m | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
434 | PP-145 |  | 1D | DAP | Smart Meter | PrePay | DAP shall be able to process & forward a service switch state request to Smart Meter | SW_state_cmd | cmd | 8AM - 8PM | 1-50 trans per 1000 DAPjm-PrePay mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
435 | PP-146 | P | [((1B + 1Aa) or 1Ab) or 1B or 7] | AMI Head End | CIS, MDMS, NMS | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
436 | PP-147 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
437 | PP-148 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from MDMS) communications failure" with Smart Meter, to MDMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
438 | PP-149 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
439 | PP-150 |  | 7 | AMI Head End | NMS | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility or MDMS) communications failure" with Smart Meter, to NMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
440 | PP-151 | P | [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [((1B + 1Aa) or 1Ab) or 1B or 7] | DAP | AMI Head-End, CIS, MDMS, NMS | PrePay | DAP shall be able to process & send "service switch operate request (from CIS - Utility, or MDMS) communications failure" with Smart Meter, to AMI Head-End and/or MDMS and/or NMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99% | < 10s | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
441 | PP-152 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & send "service switch operate request (from CIS - Utility, or MDMS) communications failure" with Smart Meter, to AMI Head-End | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99% | < 10s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
442 | PP-153 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "service switch operate request (from CIS - Utility, or MDMS) communications failure" with Smart Meter as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
443 | PP-154 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "service switch operate request (from CIS - Utility, or MDMS) communications failure" with Smart Meter as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
444 | PP-155 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "service switch operate request (from CIS - Utility, or MDMS) communications failure" with Smart Meter to AMI Head-End | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
445 | PP-156 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
446 | PP-157 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from MDMS) communications failure" with Smart Meter, to MDMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
447 | PP-158 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS shall be able to process & send "service switch operate request (from CIS - Utility) communications failure" with Smart Meter, to CIS - Utility | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
448 | PP-159 |  | 7 | AMI Head End | NMS | PrePay | AMI Head-End shall be able to process & send "service switch operate request (from CIS - Utility or MDMS) communications failure" with Smart Meter, to NMS | SW_opr_cmd_comm-err | comm-err | 8AM - 8PM | 1-4 trans per 1000 PrePay mtrs-SW-oper per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | L-M | L
449 | PP-160 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [8 or 9 or 1B or (1AA or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS, LMS, DSM | PrePay | Smart Meter shall be able to send service switch state data to CIS - Utility, MDMS, LMS, DSM | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
450 | PP-161 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter shall be able to send service switch state data to DAP | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 DAPjm-PrePay mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
451 | PP-162 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward service switch state data to AMI Head-End | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
452 | PP-163 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch state data as routed through Internet / Extranet gateway(s) - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
453 | PP-164 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch state data as routed through Internet / Extranet gateway(s) - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
454 | PP-165 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch state data with Smart Meter to AMI Head-End | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | L-M | L
455 | PP-166 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward service switch state data to CIS - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | L-M | L
456 | PP-167 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward service switch state data to MDMS | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | L-M | L
457 | PP-168 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMSshall be able to process & forward service switch state data to CIS - Utility | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | L-M | L
458 | PP-169 |  | 8 | AMI Head End | DSM | PrePay | AMI Head-End shall be able to process & forward service switch state data to DSM | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | L-M | L
459 | PP-170 |  | 9 | AMI Head End | LMS | PrePay | AMI Head-End shall be able to process & forward service switch state data to LMS | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | L-M | L
460 | PP-171 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | PrePay | Smart Meter shall be able to send service switch operate acknowledgment to CIS - Utility, MDMS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
461 | PP-172 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter shall be able to send service switch operate acknowledgment to DAP | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
462 | PP-173 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch operate acknowledgmen to AMI Head-End | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
463 | PP-174 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch operate acknowledgmen as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
464 | PP-175 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch operate acknowledgmen as routed through Internet / Extranet gateway(s) - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
465 | PP-176 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward service switch operate acknowledgment to AMI Head-End | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 30s | 10a, 10b | Y | L | L | L | Native or Intgrt | 25 |  | L | L-M | L
466 | PP-177 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward service switch operate acknowledgment to CIS - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
467 | PP-178 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS shall be able to process & forward service switch operate acknowledgment to CIS - Utility | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
468 | PP-179 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward service switch operate acknowledgment to MDMS | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 25 |  | L | L-M | L
469 | PP-180 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | PrePay | Smart Meter shall be able to send service switch operate faillure to CIS - Utility, MDMS | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 98% | < 1m | 3a, 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
470 | PP-181 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter shall be able to send service switch operate faillure to DAP | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 98% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
471 | PP-182 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward service switch operate operate faillure with Smart Meter to AMI Head-End | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
472 | PP-183 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch operate operate faillure as routed through Internet / Extranet gateway(s) - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
473 | PP-184 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward service switch operate operate faillure as routed through Internet / Extranet gateway(s) - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
474 | PP-185 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward service switch operate operate faillure to AMI Head-End | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99% | < 30s | 10a, 10b |  | L | M | L | Native or Intgrt | 50 |  | L | M | L
475 | PP-186 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward service switch operate failure to CIS - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
476 | PP-187 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward service switch operate failure to MDMS | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
477 | PP-188 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS shall be able to process & forward service switch operate failure to CIS - Utility | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 trans per 1000 SW-oper per PrePay mtrper day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 50 |  | L | M | L
478 | PP-189 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [1B or ((1B + 1Aa) or 1Ab)] | Smart Meter | CIS/Billing - Utility, MDMS | PrePay | Smart Meter shall be able to report & send metrology information after a successful service switch operate to CIS - Utility, MDMS | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 98% | < 1m | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
479 | PP-190 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter shall be able to report & send metrology information after a successful service switch operate to DAP | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
480 | PP-191 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward metrology information after a successful service switch operate to AMI Head-End | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 100 |  | L | L-M | L
481 | PP-192 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward metrology information after a successful service switch operate as routed through Internet / Extranet gateway(s) - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
482 | PP-193 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward metrology information after a successful service switch operate as routed through Internet / Extranet gateway(s) - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
483 | PP-194 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward metrology information after a successful service switch operate to AMI Head-End | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 |  | L | M | L
484 | PP-195 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward metrology information after a successful service switch operate to CIS - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
485 | PP-196 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward metrology information after a successful service switch operate to MDMS | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
486 | PP-197 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS shall be able to process & forward metrology information after a successful service switch operate to CIS - Utility | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 100 |  | L | M | L
487 | PP-198 | P | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] + 1D | CIS/Billing - Utility | Smart Meter | PrePay | CIS - Utility shall be able to send on-demand meter read request to the Smart Meter via the Head-End | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 98% | < 15s | 3a, 10a, 10b, 11 | Y | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | M | H | L
488 | PP-199 |  | 1Aa | CIS/Billing - Utility | MDMS | PrePay | CIS - Utility may be able to send on-demand meter read request to MDMS | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | L | M | L
489 | PP-200 |  | 1Ab | CIS/Billing - Utility | AMI Head-End | PrePay | CIS - Utility may be able to send on-demand meter read request to AMI Head-End | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to estimate or manually read, Not system critical | L | M | L
490 | PP-201 |  | 1B | MDMS | AMI Head-End | PrePay | MDMS shall be able to process & forward on-demand meter read request to AMI Head End, as maybe received from CIS | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 25 | May need to retry. Not system critical | L | M | L
491 | PP-202 |  | 1Ca | AMI Head End | DAP | PrePay | Head End shall be able to process & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
492 | PP-203 |  | 1Cba | AMI Head End | Internet / Extranet gateway(s) - Utility | PrePay | Head End shall be able to process & forward on-demand meter read requests as routed through Internet / Extranet gateways(s) - Utility | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
493 | PP-204 |  | 1Cb | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
494 | PP-205 |  | 1Cc | Internet / Extranet gateway(s) - Utility | DAP | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward on-demand meter read requests to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | L | M | L
495 | PP-206 |  | 1D | DAP | Smart Meter | PrePay | DAP shall be able to process & forward on-demand meter read requests to the Smart Meter (Electric or Gas, Residential or Commerical/Industrial) | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 trans per 1000 DAPjm-PrePay mtrs per day | > 98% | < 5s | 10a, 10b | Y | L | M | L | Native or Intgrt | 25 | May need to retry, Not system critical | M | M | L
496 | PP-207 | P | [(1Ab or (1B + 1Aa)) or 7] | AMI Head End | CIS/Billing - Utility, MDMS, NMS | PrePay | AMI Head-End shall be able to report & send "AMI Head-End to Smart Meter on-demand meter read request communications errors", to CIS/Billing - Utility and/or MDMS and/or NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
497 | PP-208 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End may be able to report & send "AMI Head-End to Smart Meter on-demand meter read request communications errors" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
498 | PP-209 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to report & send any "AMI Head-End to Smart Meter on-demand meter read request communications errors" to MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
499 | PP-210 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS may be able to report & send "AMI Head-End to Smart Meter on-demand meter read request communications errors" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
500 | PP-211 |  | 7 | AMI Head End | NMS | PrePay | AMI Head-End shall be able to report & send "AMI Head-End to Smart Meter on-demand meter read request communications errors" to NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 |  | L | L | L
501 | PP-212 | P | [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(1B + 1Aa) or 1Ab) or 1B or 7] | DAP | CIS/Billing - Utility, MDMS, NMS | PrePay | DAP shall be able to report & send "DAP to Smart Meter on-demand meter read request communications errors", to CIS/Billing - Utility and/or MDMS and/or NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 10s | 3a, 10a, 10b |  | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | L | L
502 | PP-213 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to report & send "DAP to Smart Meter on-demand meter read request communications errors", to AMI Head-End | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
503 | PP-214 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "DAP to Smart Meter on-demand meter read request communications errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
504 | PP-215 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "DAP to Smart Meter on-demand meter read request communications errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
505 | PP-216 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "DAP to Smart Meter on-demand meter read request communications errors" to AMI Head-End | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
506 | PP-217 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End may be able to report & send "DAP to Smart Meter on-demand meter read request communications errors" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
507 | PP-218 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS may be able to report & send "DAP to Smart Meter on-demand meter read request communications errors" to CIS - Utility | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 |  | L | M | L
508 | PP-219 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to report & send any "DAP to Smart Meter on-demand meter read request communications errors" to MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 |  | L | L | L
509 | PP-220 |  | 7 | AMI Head End | NMS | PrePay | AMI Head-End shall be able to report & send "DAP to Smart Meter on-demand meter read request communications errors" to NMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 |  | L | L | L
510 | PP-221 | P | tbd | IHD | MDMS, NMS | PrePay | IHD shall be able to report & send "IHD to Meter on-demand meter read request communications errors", to MDMS and/or NMS via comm path from IHD to meter when re-established OR alternate dataflow to NMS and/or MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 98% | tbd | tbd |  | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | L | L
511 | PP-222 | P | tbd | Cust. EMS | MDMS, NMS | PrePay | Cust. EMS shall be able to report & send "Cust. EMS to Meter on-demand meter read request communications errors", to MDMS and/or NMS via comm path from Cust. EMS to meter when re-established OR alternate dataflow to NMS and/or MDMS | on-demand_Mtr-read_cmd_comm_err | comm-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 98% | tbd | tbd | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | M | M | L
512 | PP-223 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [(1B + 1Aa) or 1Ab] | Smart Meter | CIS/Billing - Utility | PrePay | Smart Meter (Electric or Gas, Residential or Commercial/Industrial) shall be able to send on-demand meter read data to CIS - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay meter per on demand request | > 98% | < 15s | 3a, 10a, 10b | Y | L | M | L | Intgrt | 100 | May need to retry, Not system critical | M | M | L
513 | PP-224 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter (Electric or Gas, Residential or Commercial/Industrial) shall be able to send on-demand meter read data to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay meter per on demand request | > 98% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | L | M | L
514 | PP-225 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward on-demand meter read data from Smart Meter to AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 100 | May need to retry, Not system critical | L | M | L
515 | PP-226 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "on-demand meter read data from Smart Meter" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 100 | Broken cash register, Not system critical | L | M | L
516 | PP-227 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "on-demand meter read data from Smart Meter" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-PrePay mtrs per day | > 99% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 100 | Broken cash register, Not system critical | L | M | L
517 | PP-228 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "on-demand meter read data from Smart Meter" to AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 DAPjm-PrePay mtrs per day | > 99.5% | < 5s | 10a, 10b |  | L | M | L | Native or Intgrt | 100 | Broken cash register, Not system critical | L | M | L
518 | PP-229 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward on-demand meter read data to CIS - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
519 | PP-230 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward on-demand meter read data to MDMS | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
520 | PP-231 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS may be able to process & forward on-demand meter read data to CIS - Utility as received from AMI Head-End | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 trans per 1000 PrePay mtrs per day | > 99.5% | < 5s | 3a |  | L | M | L | Intgrt | 100 | May need to estimate or manually read, Not system critical | L | M | L
521 | PP-232 | P | 16Aa | ESI - Smart Meter | IHD | PrePay | Smart Meter ESI shall be able to send on-demand meter reading request to IHD via Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay meter per on demand request | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
522 | PP-233 | P | 16Ca | ESI - Smart Meter | Cust. EMS | PrePay | Smart Meter shall be able to send on-demand meter reading request to Cust. EMS via Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay meter per on demand request | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
523 | PP-234 | P | 1D + 5Bb + 16Ab | 2-Way Meter | IHD | PrePay | 2-Way Meter shall be able to send on-demand meter reading request to IHD via non Smart Meter ESI - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 98% | < 15s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
524 | PP-235 |  | 1D | 2-Way Meter | DAP | PrePay | 2-Way Meter shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
525 | PP-236 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | PrePay | DAPshall be able to process and forward on-demand meter reading request to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
526 | PP-237 |  | 16Ab | ESI - non-Smart Meter - Utility | IHD | PrePay | ESI - non-Smart Meter - Utility shall be able to process and forward on-demand meter reading request to IHD | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with IHD | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
527 | PP-238 | P | 1D + 5Bb + 16Cb | 2-Way Meter | Cust. EMS - Utility | PrePay | 2-Way Meter shall be able to send on-demand meter reading request to Cust. EMS - Utility via non Smart Meter ESI | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 98% | < 15s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
528 | PP-239 |  | 1D | 2-Way Meter | DAP | PrePay | 2-Way Meter shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
529 | PP-240 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | PrePay | DAPshall be able to process and forward on-demand meter reading request to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
530 | PP-241 |  | 16Ab | ESI - non-Smart Meter - Utility | Cust. EMS - Utility | PrePay | ESI - non-Smart Meter - Utility shall be able to process and forward on-demand meter reading request to Cust. EMS -Utility | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 trans per PrePay Customer per demand with Cust. EMS - Utility | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 100 | May need to retry, Not system critical | L | M | L
531 | PP-242 | P | 1D + [1Ca or (1Cb + 1Cba) or (1Cc + 1Cba)] + [((1B + 1Aa) or 1Ab) or 1B or 7] | Smart Meter | CIS/Billing - Utility, MDMS, NMS | PrePay | Smart Meter shall be able to report & forward Meter on-demand read request app errors to CIS/Billing - Utility and/or MDMS and/or NMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 98% | < 15s | 3a, 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
532 | PP-243 |  | 1D | Smart Meter | DAP | PrePay | Smart Meter shall be able to report & forward Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 98% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
533 | PP-244 |  | 1Ca | DAP | AMI Head-End | PrePay | DAP shall be able to process & forward Meter on-demand read request app errors to AMI Head-End | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per each DAPjm-PrePay meters' app error event | > 99% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
534 | PP-245 |  | 1Cb | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "Meter on-demand read request app errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | L | L
535 | PP-246 |  | 1Cc | DAP | Internet / Extranet gateway(s) - Utility | PrePay | DAP shall be able to process & forward "Meter on-demand read request app errors" as routed through Internet / Extranet gateway(s) - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 10a, 10b |  | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | L | L
536 | PP-247 |  | 1Cba | Internet / Extranet gateway(s) - Utility | AMI Head End | PrePay | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward "Meter on-demand read request app errors" to AMI Head-End | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99.5% | < 5s | 10a, 10b | Y | L | L | L | Native or Intgrt | 50 | Broken cash register, Not system critical | L | M | L
537 | PP-248 |  | 1Ab | AMI Head End | CIS/Billing - Utility | PrePay | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to CIS - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
538 | PP-249 |  | 1B | AMI Head End | MDMS | PrePay | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to MDMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per app error event | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | L | L
539 | PP-250 |  | 1Aa | MDMS | CIS/Billing - Utility | PrePay | MDMS may be able to process & forward Meter on-demand read request app errors to CIS - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per app error event | > 99.5% | < 5s | 3a | Y | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | M | L
540 | PP-251 |  | 7 | AMI Head End | NMS | PrePay | AMI Head-End shall be able to process & forward Meter on-demand read request app errors to NMS | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per app error event | > 99.5% | < 5s | 3a |  | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | L | L
541 | PP-252 | P | 16Ca | Smart Meter | Cust. EMS | PrePay | Smart Meter shall be able to report & send Meter on-demand read request app errors to Cust. EMS via Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 11 |  | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | L | L
542 | PP-253 | P | 16Aa | Smart Meter | IHD | PrePay | Smart Meter shall be able to report & send Meter on-demand read request app errors to IHD via Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay meter per x on-demand cmds per time period | > 99% | < 5s | 11 |  | L | L | L | Intgrt | 50 | Broken cash register, Not system critical | L | L | L
543 | PP-254 | P | 1D + 5Bb + 16Cb | 2-Way Meter | Cust. EMS - Utility | PrePay | 2-Way Meter shall be able to report & send Meter on-demand read request app errors to Cust. EMS - Utility via non-Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with Cust. EMS per x on-demand cmds per time period | > 98% | < 15s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
544 | PP-255 |  | 1D | 2-Way Meter | DAP | PrePay | 2-Way Meter shall be able to send Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with Cust. EMS per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
545 | PP-256 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | PrePay | DAPshall be able to process and forward Meter on-demand read request app errors to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with Cust. EMS per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
546 | PP-257 |  | 16Ab | ESI - non-Smart Meter - Utility | Cust. EMS - Utility | PrePay | ESI - non-Smart Meter - Utility shall be able to process and forward Meter on-demand read request app errors to Cust. EMS - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with Cust. EMS per x on-demand cmds per time period | > 99% | < 5s | 11 |  | L | L | L | Intgrt | 50 |  | L | L | L
547 | PP-258 | P | 1D + 5Bb + 16Ab | 2-Way Meter | IHD | PrePay | 2-Way Meter shall be able to report & send Meter on-demand read request app errors to IHD via non-Smart Meter ESI | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with IHD per x on-demand cmds per time period | > 98% | < 15s | 11 | Y | L | L | L | Intgrt | 50 |  | L | M | L
548 | PP-259 |  | 1D | 2-Way Meter | DAP | PrePay | 2-Way Meter shall be able to send Meter on-demand read request app errors to DAP | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with IHD per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 100 |  | L | M | L
549 | PP-260 |  | 5Bb | DAP | ESI - non-Smart Meter - Utility | PrePay | DAPshall be able to process and forward Meter on-demand read request app errors to ESI - non-Smart Meter - Utility | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with IHD per x on-demand cmds per time period | > 98% | < 5s | 11 | Y | L | L | L | Intgrt | 100 |  | L | M | L
550 | PP-261 |  | 16Ab | ESI - non-Smart Meter - Utility | IHD | PrePay | ESI - non-Smart Meter - Utility shall be able to process and forward Meter on-demand read request app errors to IHD | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 trans per PrePay customer with IHD per x on-demand cmds per time period | > 99% | < 5s | 11 |  | L | L | L | Intgrt | 100 |  | L | L | L
551 | PP-262 | P | [16Aa or (16Ab + 5Bb + 1D)] | IHD | Smart Meter | PrePay | IHD shall be able to send on-demand meter reading request to Smart Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
552 | PP-263 |  | 16Aa | IHD | Smart Meter | PrePay | IHD shall be able to send on-demand meter reading request to Smart Meter via Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with IHD | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
553 | PP-264 |  | 16Ab | IHD | ESI - non-Smart Meter - Utility | PrePay | IHD shall be able to send on-demand meter reading request to 2-Way Meter via non Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
554 | PP-265 |  | 5Bb | ESI - non-Smart Meter - Utility | DAP | PrePay | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
555 | PP-266 |  | 1D | DAP | 2-Way Meter | PrePay | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to 2Way Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with IHD | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
556 | PP-267 | P | [16Ca + (1D + 5Bb + 16Cb)] | Cust. EMS | Smart Meter | PrePay | Customer EMS shall be able to send on-demand meter reading request to Smart Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with Cust. EMS | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
557 | PP-268 |  | 16Ca | Cust. EMS | Smart Meter | PrePay | Customer EMS shall be able to send on-demand meter reading request to Smart Meter via non Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with Cust. EMS | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
558 | PP-269 |  | 16Cb | Cust. EMS | ESI - non-Smart Meter - Utility | PrePay | Customer EMS shall be able to send on-demand meter reading request to 2-Way Meter via non Smart Meter ESI | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with Cust. EMS | > 99% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
559 | PP-270 |  | 5Bb | ESI - non-Smart Meter - Utility | DAP | PrePay | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to DAP | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with Cust. EMS | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
560 | PP-271 |  | 1D | DAP | 2-Way Meter | PrePay | ESI - nob-Smart Meter - Utility shall be able to send on-demand meter reading request to 2Way Meter | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 1-10 trans per day per PrePay customer with Cust. EMS | > 98% | < 5s | 11 |  | L | M | L | Intgrt | 25 | Customer Frustration, Not system critical | L | M | L
561 | CMSG-001 | P | 2Dc + 2Ga + 2Fa | Cust. Browser - Premise | Web Portal - Utility | Cust. Info / Msgn'ng | Customer Browser - Premise shall be able to send Customer account information requests from authenticated Customer to Web Portal - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 15s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
562 | CMSG-002 |  | 2Dc + 2Ga | Cust. Browser - Premise | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | Customer Browser - Premise shall be able to send Customer account information request from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 10s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
563 | CMSG-003 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer account information requests from authenticated Customer to Web Portal - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99.5% | < 5s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
564 | CMSG-004 | P | 2Dc + 2Fb + 2Fb | Cust. Browser - Premise | Web Portal - REP | Cust. Info / Msgn'ng | Customer Browser - Premise shall be able to send Customer account information requests from authenticated Customer to Web Portal - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 15s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
565 | CMSG-005 |  | 2Dc + 2Fb | Cust. Browser - Premise | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | Customer Browser - Premise shall be able to send Customer account information request from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 10s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
566 | CMSG-006 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - Utility | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer account information requests from authenticated Customer to Web Portal - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99.5% | < 5s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
567 | CMSG-007 | P | 3Aa + 2Fa | Cust. Browser - Mobile | Web Portal - Utility | Cust. Info / Msgn'ng | Customer Browser - Mobile shall be able to send Customer account information requests from authenticated Customer to Web Portal - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 30s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
568 | CMSG-008 |  | 3Aa | Cust. Browser - Mobile | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | Customer Browser - Mobile shall be able to send Customer account information request from authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 25s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
569 | CMSG-009 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer account information requests from authenticated Customer to Web Portal - Utility | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99.5% | < 5s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
570 | CMSG-010 | P | 3Ab + 2Fb | Cust. Browser - Mobile | Web Portal - REP | Cust. Info / Msgn'ng | Customer Browser - Mobile shall be able to send Customer account information requests from authenticated Customer to Web Portal - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 30s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
571 | CMSG-011 |  | 3Ab | Cust. Browser - Mobile | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | Customer Browser - Mobile shall be able to send Customer account information request from authenticated Customer as routed through Internet / Extranet gateway(s) - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 25s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
572 | CMSG-012 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - Utility | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer account information requests from authenticated Customer to Web Portal - REP | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99.5% | < 5s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
573 | CMSG-013 | P | 2Dc + 2Wc | Cust. Browser - Premise | Common Web Portal | Cust. Info / Msgn'ng | Customer Browser - Premise shall be able to process & send Customer account information requests from authenticated Customer to Common Web Portal | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 Common Web Portal prepay mtrs per day | > 99% | < 15s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
574 | CMSG-014 | P | 2Wd | Cust. Browser - Mobile | Common Web Portal | Cust. Info / Msgn'ng | Customer Browser - Mobile shall be able to process & send Customer account information requests from authenticated Customer to Common Web Portal | Cust_Acct_Info_cmd | cmd | 7AM - 10PM | 5-15 trans per 1000 Common Web Portal prepay mtrs per day | > 99% | < 30s | 12 |  | M | M | L | Intgrt | 50 | Customer Frustration, Not system critical | M | M | L
575 | CMSG-015 | P | 2Fa + 2Ga + 2Dc | Web Portal - Utility | Cust. Browser - Premise | Cust. Info / Msgn'ng | Web Portal - Utility shall be able to send Customer account information response data to authenticated Customer Browser - Premise | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
576 | CMSG-016 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | Web Portal - Utility shall be able to process & send Customer account information response data to authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
577 | CMSG-017 |  | 2Ga + 2Dc | Internet / Extranet gateway(s) - Utility | Cust. Browser - Premise | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer account information response data to authenticated Customer Browser - Premise | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 10s | 12 |  | H | M | L | Display | 200 | Customer Frustration, Not system critical | H | M | L
578 | CMSG-018 | P | 2Fb + 2Gb + 2Dc | Web Portal - REP | Cust. Browser - Premise | Cust. Info / Msgn'ng | Web Portal - REP shall be able to send Customer account information response data to authenticated Customer Browser - Premise | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
579 | CMSG-019 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | Web Portal - REP shall be able to process & send Customer account information response data to authenticated Customeras routed through Internet / Extranet gateway(s) - REP | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
580 | CMSG-020 |  | 2Gb + 2Dc | Internet / Extranet gateway(s) - REP | Cust. Browser - Premise | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer account information response data to authenticated Customer Browser - Premise | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 10s | 12 |  | H | M | L | Display | 200 | Customer Frustration, Not system critical | H | M | L
581 | CMSG-021 | P | 2Fa + 3Aa | Web Portal - Utility | Cust. Browser - Mobile | Cust. Info / Msgn'ng | Web Portal - Utility shall be able to send Customer account information response data to authenticated Customer Browser - Mobile | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
582 | CMSG-022 |  | 2Fa | Web Portal - Utility | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | Web Portal - Utility shall be able to process & send Customer account information response data to authenticated Customer as routed through Internet / Extranet gateway(s) - Utility | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
583 | CMSG-023 |  | 3Aa | Internet / Extranet gateway(s) - Utility | Cust. Browser - Mobile | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward Customer account information response data to authenticated Customer Browser - Mobile | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 utility prepay mtrs per day | > 99% | < 25s | 12 |  | H | M | L | Display | 200 | Customer Frustration, Not system critical | H | M | L
584 | CMSG-024 | P | 2Fb + 3Ab | Web Portal - REP | Cust. Browser - Mobile | Cust. Info / Msgn'ng | Web Portal - REP shall be able to send Customer account information response data to authenticated Customer Browser - Mobile | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
585 | CMSG-025 |  | 2Fb | Web Portal - REP | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | Web Portal - REP shall be able to process & send Customer account information response data to authenticated Customer as routed through Internet / Extranet gateway(s) - REP | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99.5% | < 5s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
586 | CMSG-026 |  | 3Ab | Internet / Extranet gateway(s) - REP | Cust. Browser - Mobile | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward Customer account information response data to authenticated Customer Browser - Mobile | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 REP prepay mtrs per day | > 99% | < 25s | 12 |  | H | M | L | Display | 200 | Customer Frustration, Not system critical | H | M | L
587 | CMSG-027 | P | 2Wc + 2Dc | Common Web Portal | Cust. Browser - Premise | Cust. Info / Msgn'ng | Common Web Portal shall be able to process & send Customer account information response data to authenticated Customer Browser - Premise | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 Common Web Portal prepay mtrs per day | > 99% | < 15s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
588 | CMSG-028 | P | 2Wd | Common Web Portal | Cust. Browser - Mobile | Cust. Info / Msgn'ng | Common Web Portal shall be able to process & send Customer account information response data to authenticated Customer Browser - Mobile | Cust_Acct_Info_resp-data | resp-data | 7AM - 10PM | 5-15 trans per 1000 Common Web Portal prepay mtrs per day | > 99% | < 30s | 12 |  | H | M | L | Intgrt | 100 | Customer Frustration, Not system critical | H | M | L
589 | CMSG-029 | P | 2Aa | CIS/Billing - Utility | ODW - Utility | Cust. Info / Msgn'ng | CIS/Billing - Utility shall be able to process, extract, send bulk Customers subset of Account information to ODW - Utility | bulk_Cust_Subset_Acct_Info_Util_data | resp-data | 10pm - 6am | typically performed in x batches of y meters once per day (x) * (y) = total Smart Meters deployed per named utility | > 99.5% | < 1hr | 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
590 | CMSG-030 | P | 16 | OMS | ODW - Utility | Cust. Info / Msgn'ng | OMS shall be able to process, extract, send bulk Customers subset of service outage information to ODW - Utility | bulk_Cust_Subset_meter_outage_Info_Util_data | resp-data | 10pm - 6am | typically performed in x batches of y meters once per day | > 99.5% | < 1hr | 3a |  | M | M | L | Intgrt | xMB | Customer Frustration, Not system critical | M | M | L
591 | CMSG-031 | P | 2C | MDMS | ODW - Utility | Cust. Info / Msgn'ng | MDMS shall be able to process, extract, send bulk Customers subset of meter information to ODW - Utility | bulk_Cust_Subset_meter_Info_Util_data | resp-data | 10pm - 6am | typically performed in x batches of y meters once per day | > 99.5% | < 1hr | 3a |  | M | M | L | Intgrt | xMB | Customer Frustration, Not system critical | M | M | L
592 | CMSG-032 | P | 17 | AMI Head End | ODW - Utility | Cust. Info / Msgn'ng | AMI Head-End shall be able to process, extract, send bulk Customers subset of meter communication information to ODW - Utility | bulk_Cust_Subset_meter_comm_Info_Util_data | resp-data | 10pm - 6am | typically performed in x batches of y meters once per day | > 99.5% | < 1hr | 3a |  | L | M | L | Intgrt | xMB | Customer Frustration, Not system critical | L | M | L
593 | CMSG-033 | P | 2Ja + 2Fa | ODW - Utility | Web Portal - Utility | Cust. Info / Msgn'ng | ODW - Utility shall be able to process & send bulk Customers subset of Acct/Premise information to Web Portal - Utility | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction per day | > 99.5% | < 1hr | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
594 | CMSG-034 |  | 2Ja | ODW - Utility | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | ODW - Utility shall be able to process & send bulk Customers subset of Acct/Premise information as routed through Internet / Extranet gateway(s) - Utility | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
595 | CMSG-035 |  | 2Fa | Internet / Extranet gateway(s) - Utility | Web Portal - Utility | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward bulk Customers subset of Acct/Premise informationr to Web Portal - Utility | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
596 | CMSG-036 | P | 2Ja + 2Wa | ODW - Utility | Common Web Portal | Cust. Info / Msgn'ng | ODW - Utility shall be able to process & send bulk Customers subset of Acct/Premise information to Common Web Portal | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 1hr | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
597 | CMSG-037 |  | 2Ja | ODW - Utility | Internet / Extranet gateway(s) - Utility | Cust. Info / Msgn'ng | ODW - Utility shall be able to process & send bulk Customers subset of Acct/Premise information as routed through Internet / Extranet gateway(s) - Utility | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
598 | CMSG-038 |  | 2Wa | Internet / Extranet gateway(s) - Utility | Common Web Portal | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - Utility shall be able to inspect & forward bulk Customers subset of Acct/Premise informationr to Common Web Portal | bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
599 | CMSG-039 | P | 2Ab | CIS/Billing - REP | ODW - REP | Cust. Info / Msgn'ng | CIS/Billing - REP shall be able to process, extract, send bulk Customers subset of Account information to ODW - REP | bulk_Cust_Subset_Acct_Info_REP_data | resp-data | 10pm - 6am | typically performed in x batches of y number meters once per day (x) * (y) = total Smart Meters deployed per named REP | > 99.5% | < 1hr | 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
600 | CMSG-040 | P | 2Jb + 2Fb | ODW - REP | Web Portal - REP | Cust. Info / Msgn'ng | ODW - REP shall be able to process & send bulk Customers subset of Acct/Premise information to Web Portal - REP | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 1hr | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
601 | CMSG-041 |  | 2Jb | ODW - REP | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | ODW - REP shall be able to process & send bulk Customers subset of Acct/Premise information as routed through Internet / Extranet gateway(s) - REP | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
602 | CMSG-042 |  | 2Fb | Internet / Extranet gateway(s) - REP | Web Portal - REP | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward bulk Customers subset of Acct/Premise informationr to Web Portal - REP | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
603 | CMSG-043 | P | 2Jb + 2Wb | ODW - REP | Common Web Portal | Cust. Info / Msgn'ng | ODW - REP shall be able to process & send bulk Customers subset of Acct/Premise information to Common Web Portal | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 1hr | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
604 | CMSG-044 |  | 2Jb | ODW - REP | Internet / Extranet gateway(s) - REP | Cust. Info / Msgn'ng | ODW - REP shall be able to process & send bulk Customers subset of Acct/Premise information as routed through Internet / Extranet gateway(s) - REP | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
605 | CMSG-045 |  | 2Wb | Internet / Extranet gateway(s) - REP | Common Web Portal | Cust. Info / Msgn'ng | Internet / Extranet gateway(s) - REP shall be able to inspect & forward bulk Customers subset of Acct/Premise informationr to Common Web Portal | bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | 10pm - 6am | 1 batch transaction / day | > 99.5% | < 30m | 12, 3a |  | H | M | L | Intgrt | xMB | Customer Frustration, Not system critical | H | M | L
606 | FDAMC-001 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder VR | FeederVR_status_cmd | cmd | 24x7 | every 5 min for each VR | >99.5% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
607 | FDAMC-002 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederVR_status_cmd | cmd | 24x7 | every 5 min for each VR | >99% | < 5 sec | 2a |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
608 | FDAMC-003 |  | 4GRG | Distr SCADA FEP | Feeder VR | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder VR | FeederVR_status_cmd | cmd | 24x7 | every 5 min for each VR | >99% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
609 | FDAMC-004 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send status reply to DMS | FeederVR_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each VR | >99.5% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
610 | FDAMC-005 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederVR_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each VR | >99% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
611 | FDAMC-006 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederVR_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each VR | >99% | < 5 sec | 2a |  | L | L | M | Native or Intgrt | 50 | May need to retry | L | L | M
612 | FDAMC-007 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder VR | FeederVR_sensor_data_cmd | cmd | 24x7 | every 1 hr for each VR | >99.5% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
613 | FDAMC-008 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederVR_sensor_data_cmd | cmd | 24x7 | every 1 hr for each VR | >99% | < 5 sec | 2a |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
614 | FDAMC-009 |  | 4GRG | Distr SCADA FEP | Feeder VR | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder VR | FeederVR_sensor_data_cmd | cmd | 24x7 | every 1 hr for each VR | >99% | < 5 sec | 1b |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
615 | FDAMC-010 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send sensor data reply to DMS | FeederVR_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each VR | >99.5% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
616 | FDAMC-011 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederVR_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each VR | >99% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
617 | FDAMC-012 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederVR_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each VR | >99% | < 5 sec | 2a |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
618 | FDAMC-013 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send status change info to DMS | FeederVR_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99.5% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
619 | FDAMC-014 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederVR_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
620 | FDAMC-015 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederVR_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99% | < 5 sec | 2a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
621 | FDAMC-016 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send deviation alert to DMS | FeederVR_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99.5% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
622 | FDAMC-017 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederVR_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
623 | FDAMC-018 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederVR_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each VR | >99% | < 5 sec | 2a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alert | L | M | H
624 | FDAMC-019 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send alarm condition to DMS | FeederVR_alarm | alarm | 24x7 | Average 1 alarm every week for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
625 | FDAMC-020 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederVR_alarm | alarm | 24x7 | Average 1 alarm every week for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
626 | FDAMC-021 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederVR_alarm | alarm | 24x7 | Average 1 alarm every week for each VR | >99% | < 5 sec | 2a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
627 | FDAMC-022 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Field DA Maint - Centralized Control | Feeder VR shall be able to send failure to operate alert to DMS | FeederVR_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
628 | FDAMC-023 |  | 4GRG | Feeder VR | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder VR shall be able to send failure to operate alert (through WAN/FAN) to Distr SCADA FEP | FeederVR_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each VR | >99% | < 5 sec | 1a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
629 | FDAMC-024 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send failure to operate alert to DMS | FeederVR_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each VR | >99% | < 5 sec | 2a |  | L | M | H | Native or Intgrt | 100 | DMS will not know of alarm | L | M | H
630 | FDAMC-025 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder CBC | FeederCBC_status_cmd | cmd | 24x7 | every 5 min for each CBC | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
631 | FDAMC-026 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederCBC_status_cmd | cmd | 24x7 | every 5 min for each CBC | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
632 | FDAMC-027 |  | 4GCB | Distr SCADA FEP | Feeder CBC | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder CBC | FeederCBC_status_cmd | cmd | 24x7 | every 5 min for each CBC | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
633 | FDAMC-028 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send status reply to DMS | FeederCBC_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each CBC | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
634 | FDAMC-029 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederCBC_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each CBC | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
635 | FDAMC-030 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederCBC_status_rpsn-data | rpsn-data | 24x7 | every 5 min for each CBC | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
636 | FDAMC-031 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder CBC | FeederCBC_sensor_data_cmd | cmd | 24x7 | every 1 hr for each CBC | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
637 | FDAMC-032 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederCBC_sensor_data_cmd | cmd | 24x7 | every 1 hr for each CBC | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
638 | FDAMC-033 |  | 4GCB | Distr SCADA FEP | Feeder CBC | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder CBC | FeederCBC_sensor_data_cmd | cmd | 24x7 | every 1 hr for each CBC | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
639 | FDAMC-034 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send sensor data reply to DMS | FeederCBC_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each CBC | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
640 | FDAMC-035 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederCBC_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each CBC | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
641 | FDAMC-036 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederCBC_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 hr for each CBC | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
642 | FDAMC-037 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send status change info to DMS | FeederCBC_status_change_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
643 | FDAMC-038 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederCBC_status_change_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
644 | FDAMC-039 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederCBC_status_change_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
645 | FDAMC-040 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send deviation alert to DMS | FeederCBC_deviation_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
646 | FDAMC-041 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederCBC_deviation_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
647 | FDAMC-042 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederCBC_deviation_alert | alarm | 24x7 | Average 1 alert every 12 hr for each CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
648 | FDAMC-043 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send alarm condition to DMS | FeederCBC_alarm | alarm | 24x7 | Average 1 alarm every week for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
649 | FDAMC-044 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederCBC_alarm | alarm | 24x7 | Average 1 alarm every week for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
650 | FDAMC-045 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederCBC_alarm | alarm | 24x7 | Average 1 alarm every week for each CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
651 | FDAMC-046 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Field DA Maint - Centralized Control | Feeder CBC shall be able to send failure to operate alert to DMS | FeederCBC_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
652 | FDAMC-047 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder CBC shall be able to send failure to operate alert (through WAN/FAN) to Distr SCADA FEP | FeederCBC_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
653 | FDAMC-048 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send failure to operate alert to DMS | FeederCBC_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
654 | FDAMC-049 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Sensor | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder Sensor | FeederSensor_status_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99.5% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
655 | FDAMC-050 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederSensor_status_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 2a | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
656 | FDAMC-051 |  | 4GS | Distr SCADA FEP | Feeder Sensor | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder Sensor | FeederSensor_status_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
657 | FDAMC-052 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send status reply to DMS | FeederSensor_status_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99.5% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
658 | FDAMC-053 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederSensor_status_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
659 | FDAMC-054 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederSensor_status_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 2a | Y | L | M | M | Native or Intgrt | 50 | May need to retry | M | M | M
660 | FDAMC-055 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Sensor | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99.5% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 150 | May need to retry | M | M | M
661 | FDAMC-056 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederSensor_sensor_data_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 2a | Y | L | M | M | Native or Intgrt | 150 | May need to retry | M | M | M
662 | FDAMC-057 |  | 4GS | Distr SCADA FEP | Feeder Sensor | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 150 | May need to retry | M | M | M
663 | FDAMC-058 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send sensor data reply to DMS | FeederSensor_sensor_data_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99.5% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 250 | May need to retry | M | M | M
664 | FDAMC-059 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederSensor_sensor_data_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 1b | Y | L | M | M | Native or Intgrt | 250 | May need to retry | M | M | M
665 | FDAMC-060 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederSensor_sensor_data_rpsn-data | rpsn-data | 24x7 | every 5 sec for each Sensor | >99% | < 2 sec | 2a | Y | L | M | M | Native or Intgrt | 250 | May need to retry | M | M | M
666 | FDAMC-061 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send status change info to DMS | FeederSensor_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99.5% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
667 | FDAMC-062 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederSensor_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
668 | FDAMC-063 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederSensor_status_change_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99% | < 5 sec | 2a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
669 | FDAMC-064 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send deviation alert to DMS | FeederSensor_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99.5% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
670 | FDAMC-065 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederSensor_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
671 | FDAMC-066 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederSensor_deviation_alert | alarm | 24x7 | Average 1 alert every 1 hr for each Sensor | >99% | < 5 sec | 2a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alert | M | M | H
672 | FDAMC-067 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send alarm condition to DMS | FeederSensor_alarm | alarm | 24x7 | Average 1 alarm every day for each Sensor | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alarm | M | M | H
673 | FDAMC-068 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Sensor shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederSensor_alarm | alarm | 24x7 | Average 1 alarm every day for each Sensor | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alarm | M | M | H
674 | FDAMC-069 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederSensor_alarm | alarm | 24x7 | Average 1 alarm every day for each Sensor | >99% | < 5 sec | 2a | Y | L | M | H | Native or Intgrt | 50 | DMS will not know of alarm | M | M | H
675 | FDAMC-070 | P | 4A + [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] | DMS | Feeder Recloser | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder Recloser | FeederRecloser_status_cmd | cmd | 24x7 | every 4 hr for each Recloser | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
676 | FDAMC-071 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederRecloser_status_cmd | cmd | 24x7 | every 4 hr for each Recloser | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
677 | FDAMC-072 |  | 4GRC | Distr SCADA FEP | Feeder Recloser | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder Recloser | FeederRecloser_status_cmd | cmd | 24x7 | every 4 hr for each Recloser | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
678 | FDAMC-073 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send status reply to DMS | FeederRecloser_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Recloser | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
679 | FDAMC-074 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Recloser | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
680 | FDAMC-075 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederRecloser_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Recloser | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
681 | FDAMC-076 | P | 4A + [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] | DMS | Feeder Recloser | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder Recloser | FeederRecloser_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Recloser | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
682 | FDAMC-077 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederRecloser_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Recloser | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
683 | FDAMC-078 |  | 4GRC | Distr SCADA FEP | Feeder Recloser | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Recloser | FeederRecloser_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Recloser | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
684 | FDAMC-079 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send sensor data reply to DMS | FeederRecloser_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Recloser | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
685 | FDAMC-080 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Recloser | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
686 | FDAMC-081 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederRecloser_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Recloser | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
687 | FDAMC-082 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send status change info to DMS | FeederRecloser_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | DMS will not know of alert | M | H | H
688 | FDAMC-083 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | DMS will not know of alert | M | H | H
689 | FDAMC-084 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederRecloser_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 250 | DMS will not know of alert | M | H | H
690 | FDAMC-085 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send deviation alert to DMS | FeederRecloser_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
691 | FDAMC-086 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
692 | FDAMC-087 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederRecloser_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Recloser | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
693 | FDAMC-088 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send alarm condition to DMS | FeederRecloser_alarm | alarm | 24x7 | Average 1 alarm every week for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
694 | FDAMC-089 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_alarm | alarm | 24x7 | Average 1 alarm every week for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
695 | FDAMC-090 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederRecloser_alarm | alarm | 24x7 | Average 1 alarm every week for each Recloser | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
696 | FDAMC-091 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send failure to operate alert to DMS | FeederRecloser_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
697 | FDAMC-092 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Recloser shall be able to send failure to operate alert (through WAN/FAN) to Distr SCADA FEP | FeederRecloser_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Recloser | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
698 | FDAMC-093 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send failure to operate alert to DMS | FeederRecloser_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Recloser | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
699 | FDAMC-094 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder Switch | FeederSwitch_status_cmd | cmd | 24x7 | every 4 hr for each Switch | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
700 | FDAMC-095 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederSwitch_status_cmd | cmd | 24x7 | every 4 hr for each Switch | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
701 | FDAMC-096 |  | 4GSW | Distr SCADA FEP | Feeder Switch | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder Switch | FeederSwitch_status_cmd | cmd | 24x7 | every 4 hr for each Switch | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
702 | FDAMC-097 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send status reply to DMS | FeederSwitch_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Switch | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
703 | FDAMC-098 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Switch | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
704 | FDAMC-099 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederSwitch_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Switch | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
705 | FDAMC-100 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Switch | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
706 | FDAMC-101 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederSwitch_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Switch | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
707 | FDAMC-102 |  | 4GSW | Distr SCADA FEP | Feeder Switch | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | 24x7 | every 12 hr for each Switch | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
708 | FDAMC-103 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send sensor data reply to DMS | FeederSwitch_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Switch | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
709 | FDAMC-104 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Switch | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
710 | FDAMC-105 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederSwitch_sensor_data_rpsn-data | rpsn-data | 24x7 | every 12 hr for each Switch | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
711 | FDAMC-106 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send status change info to DMS | FeederSwitch_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
712 | FDAMC-107 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
713 | FDAMC-108 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederSwitch_status_change_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
714 | FDAMC-109 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send deviation alert to DMS | FeederSwitch_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
715 | FDAMC-110 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
716 | FDAMC-111 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederSwitch_deviation_alert | alarm | 24x7 | Average 1 alert every 1 day for each Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
717 | FDAMC-112 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send alarm condition to DMS | FeederSwitch_alarm | alarm | 24x7 | Average 1 alarm every week for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
718 | FDAMC-113 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_alarm | alarm | 24x7 | Average 1 alarm every week for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
719 | FDAMC-114 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederSwitch_alarm | alarm | 24x7 | Average 1 alarm every week for each Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
720 | FDAMC-115 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Field DA Maint - Centralized Control | Feeder Switch shall be able to send failure to operate alert to DMS | FeederSwitch_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
721 | FDAMC-116 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Switch shall be able to send failure to operate alert (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
722 | FDAMC-117 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send failure to operate alert to DMS | FeederSwitch_Operate_failure | alarm | 24x7 | Average 1 alarm every month for each Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
723 | FDAMC-118 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Fault Detector Sensor | Field DA Maint - Centralized Control | DMS shall be able to send status request to Feeder Fault_Detector | FeederFault_Detector_status_cmd | cmd | 24x7 | every 4 hr for each Fault Detector | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
724 | FDAMC-119 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send status request to Distr SCADA FEP | FeederFault_Detector_status_cmd | cmd | 24x7 | every 4 hr for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
725 | FDAMC-120 |  | 4GS | Distr SCADA FEP | Feeder Fault Detector Sensor | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status request (through WAN/FAN) to Feeder Fault_Detector | FeederFault_Detector_status_cmd | cmd | 24x7 | every 4 hr for each Fault Detector | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
726 | FDAMC-121 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Fault Detector Sensor | DMS | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send status reply to DMS | FeederFault_Detector_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Fault Detector | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
727 | FDAMC-122 |  | 4GS | Feeder Fault Detector Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send status reply (through WAN/FAN) to Distr SCADA FEP | FeederFault_Detector_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Fault Detector | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
728 | FDAMC-123 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status reply to DMS | FeederFault_Detector_status_rpsn-data | rpsn-data | 24x7 | every 4 hr for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 50 | May need to retry | M | H | M
729 | FDAMC-124 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Fault Detector Sensor | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Feeder Fault_Detector | FeederFault_Detector_sensor_data_cmd | cmd | 24x7 | every 1 week for each Fault Detector | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
730 | FDAMC-125 |  | 4A | DMS | Distr SCADA FEP | Field DA Maint - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederFault_Detector_sensor_data_cmd | cmd | 24x7 | every 1 week for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
731 | FDAMC-126 |  | 4GS | Distr SCADA FEP | Feeder Fault Detector Sensor | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Fault_Detector | FeederFault_Detector_sensor_data_cmd | cmd | 24x7 | every 1 week for each Fault Detector | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 100 | May need to retry | M | H | M
732 | FDAMC-127 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Fault Detector Sensor | DMS | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send sensor data reply to DMS | FeederFault_Detector_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 week for each Fault Detector | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 1000 | May need to retry | M | H | M
733 | FDAMC-128 |  | 4GS | Feeder Fault Detector Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederFault_Detector_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 week for each Fault Detector | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 1000 | May need to retry | M | H | M
734 | FDAMC-129 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederFault_Detector_sensor_data_rpsn-data | rpsn-data | 24x7 | every 1 week for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 1000 | May need to retry | M | H | M
735 | FDAMC-130 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Fault Detector Sensor | DMS | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send status change info to DMS | FeederFault_Detector_status_change_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 1000 | DMS will not know of alert | M | H | H
736 | FDAMC-131 |  | 4GS | Feeder Fault Detector Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send status change info (through WAN/FAN) to Distr SCADA FEP | FeederFault_Detector_status_change_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 1000 | DMS will not know of alert | M | H | H
737 | FDAMC-132 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send status change info to DMS | FeederFault_Detector_status_change_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 1000 | DMS will not know of alert | M | H | H
738 | FDAMC-133 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Fault Detector Sensor | DMS | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send deviation alert to DMS | FeederFault_Detector_deviation_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
739 | FDAMC-134 |  | 4GS | Feeder Fault Detector Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send deviation alert (through WAN/FAN) to Distr SCADA FEP | FeederFault_Detector_deviation_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
740 | FDAMC-135 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send deviation alert to DMS | FeederFault_Detector_deviation_alert | alarm | 24x7 | Average 1 alert every 1 week for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alert | M | H | H
741 | FDAMC-136 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Fault Detector Sensor | DMS | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send alarm condition to DMS | FeederFault_Detector_alarm | alarm | 24x7 | Average 1 alarm every week for each Fault Detector | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
742 | FDAMC-137 |  | 4GS | Feeder Fault Detector Sensor | Distr SCADA FEP | Field DA Maint - Centralized Control | Feeder Fault_Detector shall be able to send alarm condition (through WAN/FAN) to Distr SCADA FEP | FeederFault_Detector_alarm | alarm | 24x7 | Average 1 alarm every week for each Fault Detector | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
743 | FDAMC-138 |  | 4A | Distr SCADA FEP | DMS | Field DA Maint - Centralized Control | Distr SCADA FEP shall be able to send alarm condition to DMS | FeederFault_Detector_alarm | alarm | 24x7 | Average 1 alarm every week for each Fault Detector | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 50 | DMS will not know of alarm | M | H | H
744 | VVC-001 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | Volt/VAR - Centralized Control | DMS shall be able to send step up command to Feeder VR | FeederVR_step_up_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
745 | VVC-002 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send step up command to Distr SCADA FEP | FeederVR_step_up_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
746 | VVC-003 |  | 4GRG | Distr SCADA FEP | Feeder VR | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send step up command (through WAN/FAN) to Feeder VR | FeederVR_step_up_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
747 | VVC-004 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Volt/VAR - Centralized Control | Feeder VR shall be able to send step up command ACK to DMS | FeederVR_step_up_ack | ack | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99.5% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
748 | VVC-005 |  | 4GRG | Feeder VR | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder VR shall be able to send step up command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_step_up_ack | ack | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
749 | VVC-006 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send step up command ACK to DMS | FeederVR_step_up_ack | ack | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
750 | VVC-007 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | Volt/VAR - Centralized Control | DMS shall be able to send step down command to Feeder VR | FeederVR_step_down_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
751 | VVC-008 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send step down command to Distr SCADA FEP | FeederVR_step_down_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
752 | VVC-009 |  | 4GRG | Distr SCADA FEP | Feeder VR | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send step down command (through WAN/FAN) to Feeder VR | FeederVR_step_down_cmd | cmd | 24x7 | Average 1 cmd every 2 hr for each Feeder VR | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 250 | May need to retry | M | H | H
753 | VVC-010 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Volt/VAR - Centralized Control | Feeder VR shall be able to send step down command ACK to DMS | FeederVR_step_down_ack | ack | 24x7 | Average 1 ack every 2 hr for each Feeder VR | >99.5% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
754 | VVC-011 |  | 4GRG | Feeder VR | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder VR shall be able to send step down command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_step_down_ack | ack | 24x7 | Average 1 ack every 2 hr for each Feeder VR | >99% | < 5 sec | 1a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
755 | VVC-012 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send step down command ACK to DMS | FeederVR_step_down_ack | ack | 24x7 | Average 1 ack every 2 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | M | H | Native or Intgrt | 25 | May need to retry | M | M | H
756 | VVC-013 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | Volt/VAR - Centralized Control | DMS shall be able to send new config to Feeder VR | FeederVR_new_config_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder VR | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 500 | May need to retry | M | H | M
757 | VVC-014 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederVR_new_config_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 500 | May need to retry | M | H | M
758 | VVC-015 |  | 4GRG | Distr SCADA FEP | Feeder VR | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send new config command (through WAN/FAN) to Feeder VR | FeederVR_new_config_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder VR | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 500 | May need to retry | M | H | M
759 | VVC-016 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | Volt/VAR - Centralized Control | Feeder VR shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder VR | >99.5% | < 5 sec | 1b | Y | L | L | M | Native or Intgrt | 25 | May need to retry | M | M | M
760 | VVC-017 |  | 4GRG | Feeder VR | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder VR shall be able to send new config ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_new_config_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder VR | >99% | < 5 sec | 1b | Y | L | L | M | Native or Intgrt | 25 | May need to retry | M | M | M
761 | VVC-018 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder VR | >99% | < 5 sec | 2a | Y | L | L | M | Native or Intgrt | 25 | May need to retry | M | M | M
762 | VVC-019 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | Volt/VAR - Centralized Control | DMS shall be able to send open command to Feeder CBC | FeederCBC_open_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
763 | VVC-020 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send open command to Distr SCADA FEP | FeederCBC_open_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
764 | VVC-021 |  | 4GCB | Distr SCADA FEP | Feeder CBC | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send open command (through WAN/FAN) to Feeder CBC | FeederCBC_open_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
765 | VVC-022 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Volt/VAR - Centralized Control | Feeder CBC shall be able to send open command ACK to DMS | FeederCBC_open_ack | ack | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 25 | May need to retry | M | H | H
766 | VVC-023 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder CBC shall be able to send open command ACK (through WAN/FAN) to Distr SCADA FEP | FeederCBC_open_ack | ack | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 25 | May need to retry | M | H | H
767 | VVC-024 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send open command ACK to DMS | FeederCBC_open_ack | ack | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 25 | May need to retry | M | H | H
768 | VVC-025 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | Volt/VAR - Centralized Control | DMS shall be able to send close command to Feeder CBC | FeederCBC_close_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 150 | May need to retry | M | H | M
769 | VVC-026 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send close command to Distr SCADA FEP | FeederCBC_close_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 150 | May need to retry | M | H | M
770 | VVC-027 |  | 4GCB | Distr SCADA FEP | Feeder CBC | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send close command (through WAN/FAN) to Feeder CBC | FeederCBC_close_cmd | cmd | 24x7 | Average 1 cmd every 12 hr for each Feeder CBC | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 150 | May need to retry | M | H | M
771 | VVC-028 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Volt/VAR - Centralized Control | Feeder CBC shall be able to send close command ACK to DMS | FeederCBC_close_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder CBC | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
772 | VVC-029 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder CBC shall be able to send close command ACK (through WAN/FAN) to Distr SCADA FEP | FeederCBC_close_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder CBC | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
773 | VVC-030 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send close command ACK to DMS | FeederCBC_close_ack | ack | 24x7 | Average 1 ack every 12 hr for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
774 | VVC-031 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | Volt/VAR - Centralized Control | DMS shall be able to send new config to Feeder CBC | FeederCBC_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
775 | VVC-032 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederCBC_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
776 | VVC-033 |  | 4GCB | Distr SCADA FEP | Feeder CBC | Volt/VAR - Centralized Control | Dist SCADA shall be able to send new config (through WAN/FAN) to Feeder CBC | FeederCBC_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
777 | VVC-034 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | Volt/VAR - Centralized Control | Feeder CBC shall be able to send new config ACK to DMS | FeederCBC_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
778 | VVC-035 |  | 4GCB | Feeder CBC | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder CBC shall be able to send new config ACK (through WAN/FAN) to Dist SCADA FEP | FeederCBC_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
779 | VVC-036 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederCBC_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
780 | VVC-037 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Sensor | Volt/VAR - Centralized Control | DMS shall be able to send new config to Feeder Sensor | FeederSensor_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Sensor | >99.5% | < 5 sec | 1b | Y | L | M | M | Native or Intgrt | 500 | May need to retry | M | H | M
781 | VVC-038 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederSensor_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Sensor | >99% | < 5 sec | 2a | Y | L | M | M | Native or Intgrt | 500 | May need to retry | M | H | M
782 | VVC-039 |  | 4GS | Distr SCADA FEP | Feeder Sensor | Volt/VAR - Centralized Control | Dist SCADA shall be able to send new config (through WAN/FAN) to Feeder Sensor | FeederSensor_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Sensor | >99% | < 5 sec | 1b | Y | L | M | M | Native or Intgrt | 500 | May need to retry | M | H | M
783 | VVC-040 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | Volt/VAR - Centralized Control | Feeder Sensor shall be able to send new config ACK to DMS | FeederSensor_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Sensor | >99.5% | < 5 sec | 1b | Y | L | M | M | Native or Intgrt | 25 | May need to retry | M | M | M
784 | VVC-041 |  | 4GS | Feeder Sensor | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder Sensor shall be able to send new config ACK (through WAN/FAN) to Dist SCADA FEP | FeederSensor_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Sensor | >99% | < 5 sec | 1b | Y | L | M | M | Native or Intgrt | 25 | May need to retry | M | M | M
785 | VVC-042 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederSensor_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Sensor | >99% | < 5 sec | 2a | Y | L | M | M | Native or Intgrt | 25 | May need to retry | M | M | M
786 | VVC-043 | P | 4A + [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] | DMS | Feeder Recloser | Volt/VAR - Centralized Control | DMS shall be able to send new config to Feeder Recloser | FeederRecloser_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
787 | VVC-044 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederRecloser_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
788 | VVC-045 |  | 4GRC | Distr SCADA FEP | Feeder Recloser | Volt/VAR - Centralized Control | Dist SCADA shall be able to send new config (through WAN/FAN) to Feeder Recloser | FeederRecloser_new_config_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder CBC | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 500 | May need to retry | M | H | H
789 | VVC-046 | P | [(1Ca + 4DRC) or (4Ba + 4ERU + 4E + 4ERC) or (4F + 4FRC) or 4GRC] + 4A | Feeder Recloser | DMS | Volt/VAR - Centralized Control | Feeder Recloser shall be able to send new config ACK to DMS | FeederRecloser_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
790 | VVC-047 |  | 4GRC | Feeder Recloser | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder Recloser shall be able to send new config ACK (through WAN/FAN) to Dist SCADA FEP | FeederRecloser_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
791 | VVC-048 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederRecloser_new_config_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder CBC | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
792 | VVC-049 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | Volt/VAR - Centralized Control | DMS shall be able to send open command to Feeder Switch | FeederSwitch_open_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
793 | VVC-050 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send open command to Distr SCADA FEP | FeederSwitch_open_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
794 | VVC-051 |  | 4GSW | Distr SCADA FEP | Feeder Switch | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send open command (through WAN/FAN) to Feeder Switch | FeederSwitch_open_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
795 | VVC-052 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Volt/VAR - Centralized Control | Feeder Switch shall be able to send open command ACK to DMS | FeederSwitch_open_ack | ack | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99.5% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
796 | VVC-053 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder Switch shall be able to send open command ACK (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_open_ack | ack | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 1b | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
797 | VVC-054 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send open command ACK to DMS | FeederSwitch_open_ack | ack | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 2a | Y | L | H | M | Native or Intgrt | 25 | May need to retry | M | H | M
798 | VVC-055 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | Volt/VAR - Centralized Control | DMS shall be able to send close command to Feeder Switch | FeederSwitch_close_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99.5% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
799 | VVC-056 |  | 4A | DMS | Distr SCADA FEP | Volt/VAR - Centralized Control | DMS shall be able to send close command to Distr SCADA FEP | FeederSwitch_close_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 2a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
800 | VVC-057 |  | 4GSW | Distr SCADA FEP | Feeder Switch | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send close command (through WAN/FAN) to Feeder Switch | FeederSwitch_close_cmd | cmd | 24x7 | Average 1 cmd every 1 week for each Feeder Switch | >99% | < 5 sec | 1a | Y | L | H | H | Native or Intgrt | 150 | May need to retry | M | H | H
801 | VVC-058 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | Volt/VAR - Centralized Control | Feeder Switch shall be able to send close command ACK to DMS | FeederSwitch_close_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Switch | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
802 | VVC-059 |  | 4GSW | Feeder Switch | Distr SCADA FEP | Volt/VAR - Centralized Control | Feeder Switch shall be able to send close command ACK (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_close_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Switch | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
803 | VVC-060 |  | 4A | Distr SCADA FEP | DMS | Volt/VAR - Centralized Control | Distr SCADA FEP shall be able to send close command ACK to DMS | FeederSwitch_close_ack | ack | 24x7 | Average 1 ack every 1 week for each Feeder Switch | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
804 | DSDRC-001 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | DSDR - Centralized Control | DMS shall be able to send sensor data request to Feeder VR | FeederVR_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
805 | DSDRC-002 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederVR_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
806 | DSDRC-003 |  | 4GRG | Distr SCADA FEP | Feeder VR | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder VR | FeederVR_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | L | M | Native or Intgrt | 150 | May need to retry | L | L | M
807 | DSDRC-004 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | DSDR - Centralized Control | Feeder VR shall be able to send sensor data reply to DMS | FeederVR_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
808 | DSDRC-005 |  | 4GRG | Feeder VR | Distr SCADA FEP | DSDR - Centralized Control | Feeder VR shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederVR_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
809 | DSDRC-006 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederVR_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | M | M | Native or Intgrt | 1000 | May need to retry | L | M | M
810 | DSDRC-007 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | DSDR - Centralized Control | DMS shall be able to send step up command to Feeder VR | FeederVR_step_up_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
811 | DSDRC-008 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send step up command to Distr SCADA FEP | FeederVR_step_up_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
812 | DSDRC-009 |  | 4GRG | Distr SCADA FEP | Feeder VR | DSDR - Centralized Control | Distr SCADA FEP shall be able to send step up command (through WAN/FAN) to Feeder VR | FeederVR_step_up_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
813 | DSDRC-010 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | DSDR - Centralized Control | Feeder VR shall be able to send step up command ACK to DMS | FeederVR_step_up_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99.5% | < 2 sec | 1a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
814 | DSDRC-011 |  | 4GRG | Feeder VR | Distr SCADA FEP | DSDR - Centralized Control | Feeder VR shall be able to send step up command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_step_up_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 1a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
815 | DSDRC-012 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send step up command ACK to DMS | FeederVR_step_up_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 2a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
816 | DSDRC-013 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | DSDR - Centralized Control | DMS shall be able to send step down command to Feeder VR | FeederVR_step_down_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
817 | DSDRC-014 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send step down command to Distr SCADA FEP | FeederVR_step_down_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
818 | DSDRC-015 |  | 4GRG | Distr SCADA FEP | Feeder VR | DSDR - Centralized Control | Distr SCADA FEP shall be able to send step down command (through WAN/FAN) to Feeder VR | FeederVR_step_down_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder VR | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
819 | DSDRC-016 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | DSDR - Centralized Control | Feeder VR shall be able to send step down command ACK to DMS | FeederVR_step_down_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder VR | >99.5% | < 2 sec | 1a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
820 | DSDRC-017 |  | 4GRG | Feeder VR | Distr SCADA FEP | DSDR - Centralized Control | Feeder VR shall be able to send step down command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_step_down_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder VR | >99% | < 2 sec | 1a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
821 | DSDRC-018 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send step down command ACK to DMS | FeederVR_step_down_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder VR | >99% | < 2 sec | 2a |  | L | M | H | Native or Intgrt | 25 | May need to retry | L | M | H
822 | DSDRC-019 | P | 4A + [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] | DMS | Feeder VR | DSDR - Centralized Control | DMS shall be able to send new config to Feeder VR | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder VR | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 500 | May need to retry | L | H | M
823 | DSDRC-020 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder VR | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 500 | May need to retry | L | H | M
824 | DSDRC-021 |  | 4GRG | Distr SCADA FEP | Feeder VR | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config command (through WAN/FAN) to Feeder VR | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder VR | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 500 | May need to retry | L | H | M
825 | DSDRC-022 | P | [(1Ca + 4DRG) or (4Ba + 4ERU + 4E + 4ERG) or (4F + 4FRG) or 4GRG] + 4A | Feeder VR | DMS | DSDR - Centralized Control | Feeder VR shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder VR | >99.5% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
826 | DSDRC-023 |  | 4GRG | Feeder VR | Distr SCADA FEP | DSDR - Centralized Control | Feeder VR shall be able to send new config ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder VR | >99% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
827 | DSDRC-024 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder VR | >99% | < 5 sec | 2a |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
828 | DSDRC-025 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | DSDR - Centralized Control | DMS shall be able to send sensor data request to Feeder CBC | FeederCBC_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
829 | DSDRC-026 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederCBC_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
830 | DSDRC-027 |  | 4GCB | Distr SCADA FEP | Feeder CBC | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder CBC | FeederCBC_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
831 | DSDRC-028 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | DSDR - Centralized Control | Feeder CBC shall be able to send sensor data reply to DMS | FeederCBC_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
832 | DSDRC-029 |  | 4GCB | Feeder CBC | Distr SCADA FEP | DSDR - Centralized Control | Feeder CBC shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederCBC_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
833 | DSDRC-030 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederCBC_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
834 | DSDRC-031 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | DSDR - Centralized Control | DMS shall be able to send open command to Feeder CBC | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
835 | DSDRC-032 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send open command to Distr SCADA FEP | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
836 | DSDRC-033 |  | 4GCB | Distr SCADA FEP | Feeder CBC | DSDR - Centralized Control | Distr SCADA FEP shall be able to send open command (through WAN/FAN) to Feeder CBC | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
837 | DSDRC-034 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | DSDR - Centralized Control | Feeder CBC shall be able to send open command ACK to DMS | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 25 | May need to retry | L | H | H
838 | DSDRC-035 |  | 4GCB | Feeder CBC | Distr SCADA FEP | DSDR - Centralized Control | Feeder CBC shall be able to send open command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 25 | May need to retry | L | H | H
839 | DSDRC-036 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send open command ACK to DMS | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 25 | May need to retry | L | H | H
840 | DSDRC-037 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | DSDR - Centralized Control | DMS shall be able to send close command to Feeder CBC | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 250 | May need to retry | L | H | M
841 | DSDRC-038 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send close command to Distr SCADA FEP | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 250 | May need to retry | L | H | M
842 | DSDRC-039 |  | 4GCB | Distr SCADA FEP | Feeder CBC | DSDR - Centralized Control | Distr SCADA FEP shall be able to send close command (through WAN/FAN) to Feeder CBC | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 5 min for each Feeder CBC | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 250 | May need to retry | L | H | M
843 | DSDRC-040 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | DSDR - Centralized Control | Feeder CBC shall be able to send close command ACK to DMS | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder CBC | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
844 | DSDRC-041 |  | 4GCB | Feeder CBC | Distr SCADA FEP | DSDR - Centralized Control | Feeder CBC shall be able to send close command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder CBC | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
845 | DSDRC-042 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send close command ACK to DMS | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 5 min for each Feeder CBC | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
846 | DSDRC-043 | P | 4A + [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] | DMS | Feeder CBC | DSDR - Centralized Control | DMS shall be able to send new config to Feeder CBC | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder CBC | >99.5% | < 5 sec | 1a |  | L | H | H | Native or Intgrt | 500 | May need to retry | L | H | H
847 | DSDRC-044 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder CBC | >99% | < 5 sec | 2a |  | L | H | H | Native or Intgrt | 500 | May need to retry | L | H | H
848 | DSDRC-045 |  | 4GCB | Distr SCADA FEP | Feeder CBC | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config command (through WAN/FAN) to Feeder CBC | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder CBC | >99% | < 5 sec | 1a |  | L | H | H | Native or Intgrt | 500 | May need to retry | L | H | H
849 | DSDRC-046 | P | [(1Ca + 4DCB) or (4Ba + 4ERU + 4E + 4ECB) or (4F + 4FCB) or 4GCB] + 4A | Feeder CBC | DMS | DSDR - Centralized Control | Feeder CBC shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder CBC | >99.5% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
850 | DSDRC-047 |  | 4GCB | Feeder CBC | Distr SCADA FEP | DSDR - Centralized Control | Feeder CBC shall be able to send new config ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder CBC | >99% | < 5 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
851 | DSDRC-048 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder CBC | >99% | < 5 sec | 2a |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
852 | DSDRC-049 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Sensor | DSDR - Centralized Control | DMS shall be able to send sensor data request to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 150 | May need to retry | L | M | M
853 | DSDRC-050 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederSensor_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | M | M | Native or Intgrt | 150 | May need to retry | L | M | M
854 | DSDRC-051 |  | 4GS | Distr SCADA FEP | Feeder Sensor | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 150 | May need to retry | L | M | M
855 | DSDRC-052 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | DSDR - Centralized Control | Feeder Sensor shall be able to send sensor data reply to DMS | FeederSensor_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 250 | May need to retry | L | M | M
856 | DSDRC-053 |  | 4GS | Feeder Sensor | Distr SCADA FEP | DSDR - Centralized Control | Feeder Sensor shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederSensor_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | M | M | Native or Intgrt | 250 | May need to retry | L | M | M
857 | DSDRC-054 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederSensor_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | M | M | Native or Intgrt | 250 | May need to retry | L | M | M
858 | DSDRC-055 | P | 4A + [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] | DMS | Feeder Sensor | DSDR - Centralized Control | DMS shall be able to send new config to Feeder Sensor | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder Sensor | >99.5% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 500 | May need to retry | L | M | M
859 | DSDRC-056 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send new config command to Distr SCADA FEP | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder Sensor | >99% | < 5 sec | 2a |  | L | M | M | Native or Intgrt | 500 | May need to retry | L | M | M
860 | DSDRC-057 |  | 4GS | Distr SCADA FEP | Feeder Sensor | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config command (through WAN/FAN) to Feeder Sensor | FeederVR_new_config_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 1 hr for each Feeder Sensor | >99% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 500 | May need to retry | L | M | M
861 | DSDRC-058 | P | [(1Ca + 4DS) or (4Ba + 4ERU + 4E + 4ES) or (4F + 4FS) or 4GS] + 4A | Feeder Sensor | DMS | DSDR - Centralized Control | Feeder Sensor shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder Sensor | >99.5% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
862 | DSDRC-059 |  | 4GS | Feeder Sensor | Distr SCADA FEP | DSDR - Centralized Control | Feeder Sensor shall be able to send new config ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder Sensor | >99% | < 5 sec | 1b |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
863 | DSDRC-060 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send new config ACK to DMS | FeederVR_new_config_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 1 hr for each Feeder Sensor | >99% | < 5 sec | 2a |  | L | M | M | Native or Intgrt | 25 | May need to retry | L | M | M
864 | DSDRC-061 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | DSDR - Centralized Control | DMS shall be able to send sensor data request to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
865 | DSDRC-062 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send sensor data request to Distr SCADA FEP | FeederSwitch_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
866 | DSDRC-063 |  | 4GSW | Distr SCADA FEP | Feeder Switch | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data request (through WAN/FAN) to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 50 | May need to retry | L | H | M
867 | DSDRC-064 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | DSDR - Centralized Control | Feeder Switch shall be able to send sensor data reply to DMS | FeederSwitch_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
868 | DSDRC-065 |  | 4GSW | Feeder Switch | Distr SCADA FEP | DSDR - Centralized Control | Feeder Switch shall be able to send sensor data reply (through WAN/FAN) to Distr SCADA FEP | FeederSwitch_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
869 | DSDRC-066 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send sensor data reply to DMS | FeederSwitch_sensor_data_rpsn-data | rpsn-data | From 1-6 hr duration, from 4-8 times a year | every 15 min for each VR | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 100 | May need to retry | L | H | M
870 | DSDRC-067 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | DSDR - Centralized Control | DMS shall be able to send open command to Feeder Switch | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
871 | DSDRC-068 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send open command to Distr SCADA FEP | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
872 | DSDRC-069 |  | 4GSW | Distr SCADA FEP | Feeder Switch | DSDR - Centralized Control | Distr SCADA FEP shall be able to send open command (through WAN/FAN) to Feeder Switch | FeederVR_open_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
873 | DSDRC-070 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | DSDR - Centralized Control | Feeder Switch shall be able to send open command ACK to DMS | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
874 | DSDRC-071 |  | 4GSW | Feeder Switch | Distr SCADA FEP | DSDR - Centralized Control | Feeder Switch shall be able to send open command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
875 | DSDRC-072 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send open command ACK to DMS | FeederVR_open_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
876 | DSDRC-073 | P | 4A + [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] | DMS | Feeder Switch | DSDR - Centralized Control | DMS shall be able to send close command to Feeder Switch | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99.5% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
877 | DSDRC-074 |  | 4A | DMS | Distr SCADA FEP | DSDR - Centralized Control | DMS shall be able to send close command to Distr SCADA FEP | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 2a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
878 | DSDRC-075 |  | 4GSW | Distr SCADA FEP | Feeder Switch | DSDR - Centralized Control | Distr SCADA FEP shall be able to send close command (through WAN/FAN) to Feeder Switch | FeederVR_close_cmd | cmd | From 1-6 hr duration, from 4-8 times a year | Average 1 cmd every 12 hr for each Feeder Switch | >99% | < 2 sec | 1a |  | L | H | H | Native or Intgrt | 250 | May need to retry | L | H | H
879 | DSDRC-076 | P | [(1Ca + 4DSW) or (4Ba + 4ERU + 4E + 4ESW) or (4F + 4FSW) or 4GSW] + 4A | Feeder Switch | DMS | DSDR - Centralized Control | Feeder Switch shall be able to send close command ACK to DMS | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 12 hr for each Feeder Switch | >99.5% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
880 | DSDRC-077 |  | 4GSW | Feeder Switch | Distr SCADA FEP | DSDR - Centralized Control | Feeder Switch shall be able to send close command ACK (through WAN/FAN) to Distr SCADA FEP | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 12 hr for each Feeder Switch | >99% | < 2 sec | 1b |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M
881 | DSDRC-078 |  | 4A | Distr SCADA FEP | DMS | DSDR - Centralized Control | Distr SCADA FEP shall be able to send close command ACK to DMS | FeederVR_close_ack | ack | From 1-6 hr duration, from 4-8 times a year | Average 1 ack every 12 hr for each Feeder Switch | >99% | < 2 sec | 2a |  | L | H | M | Native or Intgrt | 25 | May need to retry | L | H | M

## row-cnt-payload-usecase
Count of Rqmt Ref | Use Case Ref
Payload Name - Specific Data/Mesg (Logical - info content the same) | Cust. Info / Msgn'ng | DSDR - Centralized Control | Field DA Maint - Centralized Control | Meter reading | PHEV | PrePay | Service Switch | Volt/VAR - Centralized Control | Grand Total
bulk_Cust_Subset_Acct_Info_REP_data | 1 | [7 empty] | 1
bulk_Cust_Subset_Acct_Info_Util_data | 1 | [7 empty] | 1
bulk_Cust_Subset_Acct_Premise_Info_REP_data | 6 | [7 empty] | 6
bulk_Cust_Subset_Acct_Premise_Info_Util_data | 6 | [7 empty] | 6
bulk_Cust_Subset_meter_comm_Info_Util_data | 1 | [7 empty] | 1
bulk_Cust_Subset_meter_Info_Util_data | 1 | [7 empty] | 1
bulk_Cust_Subset_meter_outage_Info_Util_data | 1 | [7 empty] | 1
bulk_Mtr-read_cmd |  |  |  | 2 |  |  |  |  | 2
bulk_Mtr-read_resp-data |  |  |  | 2 |  |  |  |  | 2
Cust_Acct_Info_cmd | 14 | [7 empty] | 14
Cust_Acct_Info_resp-data | 14 | [7 empty] | 14
FeederCBC_alarm |  |  | 3 | [5 empty] | 3
FeederCBC_close_ack | [7 empty] | 3 | 3
FeederCBC_close_cmd | [7 empty] | 3 | 3
FeederCBC_deviation_alert |  |  | 3 | [5 empty] | 3
FeederCBC_new_config_ack | [7 empty] | 3 | 3
FeederCBC_new_config_cmd | [7 empty] | 3 | 3
FeederCBC_open_ack | [7 empty] | 3 | 3
FeederCBC_open_cmd | [7 empty] | 3 | 3
FeederCBC_Operate_failure |  |  | 3 | [5 empty] | 3
FeederCBC_sensor_data_cmd |  | 3 | 3 | [5 empty] | 6
FeederCBC_sensor_data_rpsn-data |  | 3 | 3 | [5 empty] | 6
FeederCBC_status_change_alert |  |  | 3 | [5 empty] | 3
FeederCBC_status_cmd |  |  | 3 | [5 empty] | 3
FeederCBC_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederFault_Detector_alarm |  |  | 3 | [5 empty] | 3
FeederFault_Detector_deviation_alert |  |  | 3 | [5 empty] | 3
FeederFault_Detector_sensor_data_cmd |  |  | 3 | [5 empty] | 3
FeederFault_Detector_sensor_data_rpsn-data |  |  | 3 | [5 empty] | 3
FeederFault_Detector_status_change_alert |  |  | 3 | [5 empty] | 3
FeederFault_Detector_status_cmd |  |  | 3 | [5 empty] | 3
FeederFault_Detector_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederRecloser_alarm |  |  | 3 | [5 empty] | 3
FeederRecloser_deviation_alert |  |  | 3 | [5 empty] | 3
FeederRecloser_new_config_ack | [7 empty] | 3 | 3
FeederRecloser_new_config_cmd | [7 empty] | 3 | 3
FeederRecloser_Operate_failure |  |  | 3 | [5 empty] | 3
FeederRecloser_sensor_data_cmd |  |  | 3 | [5 empty] | 3
FeederRecloser_sensor_data_rpsn-data |  |  | 3 | [5 empty] | 3
FeederRecloser_status_change_alert |  |  | 3 | [5 empty] | 3
FeederRecloser_status_cmd |  |  | 3 | [5 empty] | 3
FeederRecloser_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederSensor_alarm |  |  | 3 | [5 empty] | 3
FeederSensor_deviation_alert |  |  | 3 | [5 empty] | 3
FeederSensor_new_config_ack | [7 empty] | 3 | 3
FeederSensor_new_config_cmd | [7 empty] | 3 | 3
FeederSensor_sensor_data_cmd |  | 3 | 3 | [5 empty] | 6
FeederSensor_sensor_data_rpsn-data |  | 3 | 3 | [5 empty] | 6
FeederSensor_status_change_alert |  |  | 3 | [5 empty] | 3
FeederSensor_status_cmd |  |  | 3 | [5 empty] | 3
FeederSensor_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederSwitch_alarm |  |  | 3 | [5 empty] | 3
FeederSwitch_close_ack | [7 empty] | 3 | 3
FeederSwitch_close_cmd | [7 empty] | 3 | 3
FeederSwitch_deviation_alert |  |  | 3 | [5 empty] | 3
FeederSwitch_open_ack | [7 empty] | 3 | 3
FeederSwitch_open_cmd | [7 empty] | 3 | 3
FeederSwitch_Operate_failure |  |  | 3 | [5 empty] | 3
FeederSwitch_sensor_data_cmd |  | 3 | 3 | [5 empty] | 6
FeederSwitch_sensor_data_rpsn-data |  | 3 | 3 | [5 empty] | 6
FeederSwitch_status_change_alert |  |  | 3 | [5 empty] | 3
FeederSwitch_status_cmd |  |  | 3 | [5 empty] | 3
FeederSwitch_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederVR_alarm |  |  | 3 | [5 empty] | 3
FeederVR_close_ack |  | 6 | [6 empty] | 6
FeederVR_close_cmd |  | 6 | [6 empty] | 6
FeederVR_deviation_alert |  |  | 3 | [5 empty] | 3
FeederVR_new_config_ack |  | 9 | [5 empty] | 3 | 12
FeederVR_new_config_cmd |  | 9 | [5 empty] | 3 | 12
FeederVR_open_ack |  | 6 | [6 empty] | 6
FeederVR_open_cmd |  | 6 | [6 empty] | 6
FeederVR_Operate_failure |  |  | 3 | [5 empty] | 3
FeederVR_sensor_data_cmd |  | 3 | 3 | [5 empty] | 6
FeederVR_sensor_data_rpsn-data |  | 3 | 3 | [5 empty] | 6
FeederVR_status_change_alert |  |  | 3 | [5 empty] | 3
FeederVR_status_cmd |  |  | 3 | [5 empty] | 3
FeederVR_status_rpsn-data |  |  | 3 | [5 empty] | 3
FeederVR_step_down_ack |  | 3 | [5 empty] | 3 | 6
FeederVR_step_down_cmd |  | 3 | [5 empty] | 3 | 6
FeederVR_step_up_ack |  | 3 | [5 empty] | 3 | 6
FeederVR_step_up_cmd |  | 3 | [5 empty] | 3 | 6
Mtr-read_multi-interval-data_cmd |  |  |  | 7 |  |  |  |  | 7
Mtr-read_multi-interval-data_resp-data |  |  |  | 25 |  |  |  |  | 25
on-demand_Mtr-read_cmd |  |  |  | 19 |  | 19 |  |  | 38
on-demand_Mtr-read_cmd_comm_err |  |  |  | 11 |  | 16 |  |  | 27
on-demand_Mtr-read_cmd_err |  |  |  | 20 |  | 20 |  |  | 40
on-demand_Mtr-read_resp-data |  |  |  | 19 |  | 19 |  |  | 38
PHEV_price_rate_cmd |  |  |  |  | 11 |  |  |  | 11
PHEV_price_rate_comm_err |  |  |  |  | 20 |  |  |  | 20
PHEV_pwr_chrg_rate_comm_err |  |  |  |  | 18 |  |  |  | 18
PHEV_pwr_chrg_rate_negot-thrd |  |  |  |  | 22 |  |  |  | 22
PHEV_pwr_chrg_status_resp-data |  |  |  |  | 11 |  |  |  | 11
PHEV_Vin_data_cmd |  |  |  |  | 11 |  |  |  | 11
PHEV_Vin_data_comm_err |  |  |  |  | 10 |  |  |  | 10
prepay_cust_enroll_cmd | [5 empty] | 28 |  |  | 28
prepay_cust_unenroll_cmd | [5 empty] | 28 |  |  | 28
prepay_meter_config_cmd | [5 empty] | 9 |  |  | 9
prepay_msg_[1of10]_resp-data | [5 empty] | 52 |  |  | 52
SW_opr_cancel_cmd | [5 empty] | 9 | 6 |  | 15
SW_opr_cmd | [5 empty] | 10 | 9 |  | 19
SW_opr_cmd_ack | [5 empty] | 9 | 9 |  | 18
SW_opr_cmd_comm-err | [5 empty] | 14 | 9 |  | 23
SW_opr_fail_cmd-err | [5 empty] | 9 | 9 |  | 18
SW_post-oper-info_resp-data | [5 empty] | 9 | 9 |  | 18
SW_state_cmd | [5 empty] | 9 | 9 |  | 18
SW_state_cmd_resp-data | [5 empty] | 11 | 11 |  | 22
Grand Total | 45 | 78 | 138 | 105 | 103 | 271 | 71 | 60 | 871