## Meter Reading
Meter reading
Applicable Use cases
Requirements
Meter reading | CIS
Meter reading | CIS shall be able to obtain meter read information from the MDMS
Meter reading
Meter reading
Meter reading | MDMS
Meter reading | MDMS shall be able to forward the meter read request from the CIS
Meter reading | MDMS shall be able to support reading meters from a Head End system
Meter reading | MDMS shall be able to report last known meter read on failure
Meter reading
Meter reading | Head End
Meter reading | Head End shall be able to read meters on request from the mdms
Meter reading | Head End shall be able to report on request read commnication failure to the mdms
Meter reading | Head End shall be able to report meter read errors to the MDMS
Meter reading | Head End shall be able to obtain meters data on a configurable schedule
Meter reading | Head End shall be able to report meter data on a configurable schedule
Meter reading
Meter reading | WAN
Meter reading | WAN shall be able to support network traffic associated with meter reading
Meter reading
Meter reading | Assumption: AP could store and forward, act as an access point or route
Meter reading | AP
Meter reading | AP shall be able to forward on demand read request from the head end to the meter
Meter reading | AP shall be able to forward on demand read response from meter to head end
Meter reading | AP shall be able to report on demand communication failure to the head end
Meter reading | AP shall be able to forward scheduled meter data reports to the head end
Meter reading
Meter reading | NAN
Meter reading | NAN shall be able to support network traffic associated with meter reading
Meter reading
Meter reading | Meter NIC
Meter reading | Meter NIC shall be able to obtain on demand read information from the metrology
Meter reading | Meter NIC shall be able to report on demand communication failure
Meter reading | Meter NIC shall be able to report communication failure with the metrology
Meter reading | Meter NIC shall be able to report when scheduled
Meter reading
Meter reading | Metrology
Meter reading
Meter reading | Meter Switch
Meter reading
Meter reading | ESI

## Service Switch
Service Switch
Requirements
CIS
Service Switch | CIS shall be able to send a service switch operation request
Service Switch | CIS shall be able to request service switch status
Service Switch | CIS shall be able to send a scheduled switch operation request
Service Switch | CIS shall be able to cancel a scheduled switch operation request
MDMS
Service Switch | MDMS shall be able to forward a service switch operation request
AMS
Service Switch | AMS shall be able to request service switch status
DMS
DSM
Service Switch | DSM shall be able to accept service switch state of meters
LMS
Service Switch | LMS shall be able to accept service switch state of meters
HEAD END
Service Switch | Head End shall be able to change service switch state
Service Switch | Head End shall be able to request service switch status
Service Switch | Head end shall be able to report communication failure with the next lower layer
Service Switch | WAN
Service Switch | WAN shall be able to support network traffic associated with Service Switch operations
Service Switch | AP
Service Switch | AP shall be able to forward on change service switch state request from the head end to the meter
Service Switch | AP shall be able to report communication failure with the next lower layer
NAN
Service Switch | NAN shall be able to support network traffic associated with Service Switch operations
METER NIC
Service Switch | Meter Nic shall accept change service switch operations from the AP
Service Switch | Meter Nic shall accept service switch status request from the AP
Service Switch | Meter Nic may be able to report metrology information after a successful service switch operation
Service Switch | Meter NIC shall be able to report failure of service switch operation
Service Switch | Meter NIC shall be able to report successful service switch operation
Metrology
Meter Switch

## Combined
Rqmt Ref (auto num) | SG-Net Data Flow Ref | Potential NISTIR Data Flow X-Ref | Use Case Ref | Requirements | Specific Data/Mesg Payload Name | How Often | Reliability | Latency Rqmts | Security | Payload Size | Edit Notes
GIS
4 |  |  | WFM | Shall be able to receive request for GIS information for single and multiple assets and systems |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
5 |  |  | WFM | Shall be able to communicate requested GIS information about assets to requestors |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min |  | split into separate requirements
6 |  |  | WFM | shall be able to receive update information form from field force or field force information system |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
7 |  |  | Distr Auto | Shall be able to receive request for GIS information for single and multiple assets and systems |  | 1000's to 1,000,000 trans per day pending size of utility | > 99.5% | 5ms to 5 min |  |  | remove, duplicates the WFM 4 ref above
8 |  |  | Distr Auto | Shall be able to communicate requested GIS information about assets to requestors |  | 1000's to 1,000,000 trans per day pending size of utility | > 99.5% | 5ms to 5 min |  |  | remove, duplicates the WFM 5 ref above
9 | 13 |  | Distr Auto | shall be able to receive update information form Distribution Automation information systems |  | 1000's to 1,000,000 trans per day pending size of utility | > 99.5% | 5ms to 24 hrs |  |  | do we use WFM 6 above or this one?
10
AMS
12 |  |  | Service Switch | AMS shall be able to request service switch status from what actor(s) [needs to be spelled out]? | SW_status req | 1 trans per 1000 mtrs per day | > 98% | 5ms to 1 hr
13 |  |  | WFM | Shall be able to receive request for asset information from single or multiple other named [these need to be spelled out] actors |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 1hr
14 |  |  | WFM | Shall be able to reply to information request - including single queries and reports |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5s
15 |  |  | WFM | Shall be able to receive asset updates from other information systems |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 1hr
16 |  |  | Distr Auto | Shall be able to receive request for asset information |  | 1 trans per 1000 mtrs per day | > 99.5% | 5ms to 1hr |  |  | do we use WFM 13 above or this one?
17 |  |  | Distr Auto | Shall be able to reply to information request - including single queries and reports |  | 1 trans per 1000 mtrs per day | > 99.5% | 5ms to 1hr |  |  | do we use WFM 14 above or this one?
18 |  |  | Distr Auto | Shall be able to receive asset updates from other information systems |  | 1 trans per 1000 mtrs per day | > 99.5% | 5ms to 1hr |  |  | do we use WFM 15 above or this one?
19
Web Portal
21 | 2Aa, 2Ab, 2Fa, 2Fb, 2Fc |  | Pre-Pay | Web Portal shall be able to receive & respond to specific Customer account information requests from the authenticated customer and/or the Customers' REP. | Cust_Acct_Info req & rpns | 1-3 trans per 100 mtrs per day | > 99% | 5ms to 15s
22 | 2Aa, 2Ab, 2Da, 2Dc, 2Fa, 2Fb |  | Pre-Pay | Web Portal shall be able to receive & forward specific Customer Prepay requests to CIS |  | 1 -3 trans per 100 mtrs per day | > 99% | 5ms to 15s
23
CIS (including Billing)
25 | 1Ab, 1C, 1D |  | Meter reading | CIS shall be able to obtain meter read information on demand from the Smart Meter via the Head-End | on-demand_Mtr-read_data req & rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 5s
26 | 1Aa |  | Meter reading | CIS shall be able to obtain meter read information from the MDMS for billing (In-Bulk) | bulk_Mtr-read_data req & rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 1hr |  |  | this indicates billing is a part of CIS, but HISTR & Nist diagrams have billing separate from CIS(?)
27 | 1Ab, 1B, 1C, 1D |  | Service Switch / Pre-Pay | CIS shall be able to send a service switch operation request to the Smart Meter via the Head-End | SW_opr req | 1-50 trans per 1000 mtrs per day | > 99% | < 1 hr
28 | 1Ab, 1C, 1D |  | Service Switch / Pre-Pay | CIS shall be able to request service switch status from Smart Meter via the Head-End | SW_status req | 1-50 trans per 1000 mtrs per day | > 99% | 5ms to 10s
29 |  |  | Service Switch | CIS shall be able to send a service switch operation request |  | 1-50 trans per 1000 mtrs per day | > 99% | < 1min |  |  | remove, use service switch item 27
30 | 1Ab, 1B, 1C, 1D |  | Service Switch | CIS shall be able to cancel a scheduled switch operation request to Smart Meter via Head-End | SW_opr_cancel req | 1-50 trans per 1000 mtrs per day | > 99% | < 1min
31 |  |  | WFM | Shall be able to receive request for information from external informations systems [need to name those external systems] |  | 1 trans per 1000 mtrs per day | > 99% | < 5s
32 |  |  | WFM | Shall be able to receive request for information from staff and field force workers [and other named actors] |  | 1 trans per 1000 mtrs per day | > 99% | < 5s
33 |  |  | WFM | Shall be able to respond with requested information to requestor [need to list named requestors] |  | 1 trans per 1000 mtrs per day | > 99% | < 5s
34 |  |  | Pre-Pay | CIS shall be able to obtain scheduled Meter read information |  | 25 trans per 1000 mtrs per day | > 99% | < 5s |  |  | remove, duplicates Meter reading item 26
35 |  |  | Pre-Pay | CIS shall be able to obtain on-demand Meter read information |  | 5 trans per 1000 mtrs per day | > 99% | < 5s |  |  | remove, duplicates Meter reading item 25
36 | 1Aa, 1Ab |  | Pre-Pay | CIS shall be able to send a Smart Meter reconfig request for C12.19 prepay tables & load control directives | prepay_C12-19_set req; prepay_load_cntl_dir req | 25 trans per 1000 mtrs per day | > 99% | <10s to <30s
37 | 2Aa, 2Ab, 2Da, 2Dc, 2Fa, 2Fb |  | Pre-Pay | CIS shall be able to process/send Customer account information as requested from authenticated Customer or REP via Web Portal | Cust_Acct_Info req & rpns | 25 trans per 1000 mtrs per day | > 99% | <10s
38 | 2Aa, 2Ab, 2Da, 2Dc, 2Fa, 2Fb |  | Pre-Pay | CIS shall be able to receive/process Prepay enrollment/un-enrollment requests coming from authenticated Customer via phone in or Web Portal | prepay_enroll req; prepay_unenroll req; | 25 trans per 1000 mtrs per day | > 99% | <10s
39 | 1Aa, 1Ab, 1B, 1C, 1D, 2Aa, 2Ab, 2Da, 2dc, 2Fa, 2Fb, 3Aa, 3Aax, 3Ab, 3Abx, 3By, 5Bb, 16Ba, 16Bb |  | Pre-Pay | CIS shall be able to send Prepay messages (~10 different types) to Customer via 1 or combo of IHD via Head-End, SMS Text message, Web Portal, e-mail, automated phone calling service via Internet or extranets | prepay_msg_[1-10] | 25 trans per 1000 mtrs per day | > 99% | <10s - 5m |  |  |  | Delay |  | Bit rate (bandwitdh) |  |  |  | Reliability |  | Link connectivity |  |  | Security
40 |  |  | Pre-Pay | CIS shall be able to receive/post Customer account payments coming from multple sources (internal or 3rd party to CIS operator) | Cust_Acct_paymt | 25 trans per 1000 mtrs per day | > 99% | <10s - 2hr |  |  |  | Maximum | Jitter | Data size | Frequency | Minimum | Maximum | outage | loss | Point-to-point | Point-to-multipoint | Multipoint-to-multipoint | Accountability | Assurance | Availability | Confidentiality | Data integrity
41 | 1Aa, 1Ab |  | Pre-Pay | CIS shall be able to send a PrePay associate request to Premise Meter request to MDMS or Head End | prepay_mtr_flag req | 25 trans per 1000 mtrs per day | > 99% | <10s |  |  |  | s | s | bit | s | bit/s | bit/s | % / ratio | % / ratio | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No
42 | 2B, 2Da, 2Dc, 3Aa, 3Aax, 3Ab, 3Abx, 3By, 5Bc |  | Pre-Pay | CIS shall be able to send Prepay messages (~10 different types) to Customer via 1 or combo of IHD [via 3rd party], SMS Text message, Web Portal, e-mail, automated phone calling service via Internet or extranets | prepay_msg_[1-10] | 25 trans per 1000 mtrs per day | > 99% | <10s - 5m |  |  |  | 1-5s
43
EMS
45 | 15 |  | Distr Auto | Shall be able to exchange informaton with the Distribution Management System (DMS) |  | 1000's to 1,000,000 trans per day pending size of utility | > 99.5% | <10s
46
DMS
48 | 4Aa, 4Ab, 4Ba, 4Bb |  | Distr Auto | Shall be able to communicate request for information and status to Distribution system assets [really should list the assets] |  | 1000's to 1,000,000 trans per day depending on qty of DA devices and DMS enabled functions | > 99% | <5s - 2m
49 | 4Aa, 4Ab, 4Ba, 4Bb |  | Distr Auto | Shall be able to receive information and status from Distribution systems assets |  | 1000's to 1,000,000 trans per day pending size of utility | > 99% | <5s
50 | 4Aa, 4Ab, 4Ba, 4Bb |  | Distr Auto | Shall be able to communicate request for action to Distribution system assets | DA_device_cmd req | 100's to 100,000's trans per day pending size of utility | > 98% depending on device type | <5s | Need to further clarify between cap bank versus reclosures
51 | 4Aa, 4Ab, 4Ba, 4Bb |  | Distr Auto | Shall be able to receive confirmation of actions taken by Distribution system assets | DA_device_cmd rpns | 100's to 100,000's trans per day pending size of utility | > 98% depending on device type | <5s
52 |  |  | Distr Auto | Shall be able to communicate request for information and status to other [need to name] Distribution informaton systems |  | 1000's to 1,000,000 trans per day depending on qty of DA devices and DMS enabled functions | > 99% | <5s - 2m
53 |  |  | Distr Auto | Shall be able to receive information and status from other Distribution information systems |  | 1000's to 1,000,000 trans per day pending size of utility | > 99% | <5s
54 |  |  | Distr Auto | Shall be able to communicate request for action to other Distribution information systems |  | 1000's to 1,000,000 trans per day pending size of utility | > 99% | <5s
55 |  |  | Distr Auto | Shall be able to receive confirmation of actions taken by other Distribution information systems |  | 1000's to 1,000,000 trans per day pending size of utility | > 99% | <5s
56
DSM
58 |  |  | Service Switch | DSM shall be able to accept service switch state of Smart Meters from [named] actors | SW_status rpns | 1-50 trans per 1000 mtrs per day | > 99% | <5s - <1m
59 | 11 |  | Distr Auto | Shall be able to exchange informaton with the Distribution Management System (DMS) |  | 1000's to 1,000,000 trans per day depending upon qty of end devices and enabled DSM/DMS functions | > 99% | <5s - <5m
60
LMS
62 |  |  | Service Switch | LSM shall be able to accept service switch state of Smart Meters from [named] actors | SW_status rpns | 1-50 trans per 1000 mtrs per day | > 99% | <5s
63 | 9 |  | PHEV | LMS shall be able to communicate with the Head End for re-charging rate of PHEV | PHEV_chrg_rate req | ACTION: Jerry Armes
64 | 9 |  | PHEV | LMS shall be able to communicate with the Head End for price for PHEV | PHEV_price req | ACTION: Jerry Armes
65 | 1C, 1D, 2G, 5Bb, 5Bc, 9, 16Aa, 16Ab |  | Load MGMT | Shall be able to send (reliable?) multicast or unicast load control messages to [named] actors | load_cntrl_msg req | 1,000,000's trans pending utility size | > 99% | <15m
66 | 1C, 1D, 2G, 5Bb, 5Bc, 9, 16Aa, 16Ab |  | Load MGMT | Shall be able to receive verification of control messages from [named] actors | load_cntrl_msg ack | 1,000,000's trans pending utility size | > 99% | < 1hr
67 |  |  | Load MGMT | Shall be able to send load control messages to the Distribution system demand response (DSDR) [is this a new actor?] | load_cntrl_msg req | 1000's to 1,000,000 trans per day pending size of utility | > 99.5% | < 5s
68 | 12 |  | Distr Auto | Shall be able to exchange informaton with the Distribution Management System (DMS) |  | 1000's to 1,000,000 trans per day depending upon qty of end devices and enabled LSM/DMS functions | > 99.5% | <5s - <5m
69
Event/OMS
71 | 14 |  | WFM | Shall be able to communicate outage infromation to the workforce dispatch system [<-- is this WFM or a new actor?] |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
72 |  |  | WFM | Shall be able to receive request for informanton and status about an event or an outage from [named] actors |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
73 |  |  | WFM | Shall be able to respond with requested information to [named] requestor(s) |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
74 | 14 |  | WFM | Shall be able to receive updates from field force and field force information systems [<-- is this WFM or new actors, need to name them?] |  | 1 trans per 1000 mtrs per day | > 99% | 5ms to 5 min
75
MDMS
77 | 1B |  | Meter reading | MDMS shall be able to forward on demand meter read request from the CIS | on-demand_Mtr-read_data req | 25 trans per 1000 mtrs per day | > 99.5% | < 5s |  |  | Only if MDMS is the Only actor that acts as the CIS proxy to communicate with Head-End.
78 | 1B |  | Meter reading | MDMS shall be able to support bulk PULL/PUSH Smart Meter demand interval reading meters from a via the Head End system | bulk_Mtr-read_data [req] & rpns | 4-6 bulk meter read operations per day | > 99.5% | < 1hr
79 |  |  | Meter reading | MDMS shall be able to report last known meter read on failure obtaining reading on demand [need to clarify this functional requirement as currently written] |  | 1 trans per 1000 mtrs per day | > 99.5% | < 10s
80 | 1B |  | Service Switch | MDMS shall be able to forward a service switch operation request | SW_opr req | 1-50 trans per 1000 mtrs per day | > 99.5% | < 15m |  |  | Only if MDMS is the Only actor that acts as the CIS proxy to communicate with Head-End.
81 | 1B |  | PHEV | MDMS shall be able to communicate with the Head End Vin number information [is PHEV Vin info only stored in MDMS or in someother actor e.g. CIS?] | PHEV_Vin_data rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s
82 | 6 |  | WFM | Shall be able to communicate problems detected with an end device (i.e. meter) to the workforce dispatch system [is workforce dispatch WFM? And must all actors comm with MDMS for this data?] |  | 1 trans per 2000 mtrs per day | > 99.5% | < 15m |  |  | This appears to assumes MDMS is the main data store for all things concerning end devices (even operational), architecturally, I expect the Head-End to direct the operational problem events to the correct actor based on use of enterprise bus versus assuming that it all gets stored in MDMS and then all other actors that consume the various event data must go to MDMS
83 | 6 |  | WFM | Shall be able to communicate service request to the workforce dispatch system | work_force_srvc req | 1 trans per 2000 mtrs per day | > 99.5% | < 15m |  |  | Ron Cunningham: I expect service requests to come out of other backoffice actors to route to the actor(s) where the tickets are manged/scheduled/dispatched, not MDMS being the primary.
84 |  |  | WFM | Shall be able to receive meter system updates from other information systems [need to name the other actors] |  | 1 trans per 2000 mtrs per day | > 99.5% | < 15m
85 | 1B, 1C, 1D |  | Pre-Pay | MDMS may be able to request on-demand Smart Meter meter reads via Head-End | on-demand_Mtr-read_data req | 25 trans per 1000 mtrs per day | > 99% | <10s
86 | 1B, 1C, 1D |  | Pre-Pay | MDMS shall be able to support receiving on-demand Smart Meter meter readings via Head-End | on-demand_Mtr-read_data rpns | 25 trans per 1000 mtrs per day | > 99% | <10s
87 | 1B |  | Pre-Pay | MDMS may be able to forward a Meter SW open/close operation request | SW_opr req | 25 trans per 1000 mtrs per day | > 99% | <10s |  |  | Only if MDMS is the Only actor that acs as the CIS proxy to communicate with Head-End
88 | 1B |  | Pre-Pay | MDMS shall be able to support receiving Smart Meter switch status | SW_status rpns | 25 trans per 1000 mtrs per day | > 99% | <10s
89 | 2C |  | Pre-Pay | MDMS shall be able to process/send meter read information as requested by authenticated Customer via Web Portal | on-demand_Mtr-read_data req & rpns: bulk_Mtr-read_data [req] & rpns | 25 trans per 1000 mtrs per day | > 99% | <10s - <1m |  | review with line 90
90 | 2C |  | Pre-Pay | MDMS shall be able to process/send meter read information as requested by authenticated Customer via 3rd-party Web Portals | on-demand_Mtr-read_data req & rpns: bulk_Mtr-read_data [req] & rpns | 25 trans per 1000 mtrs per day | > 99% | <10s - <1m
91
AMI Head End
93 | 1C, 1D |  | Meter reading | Head End shall be able to process on demand read meters on demand request from the mdms MDMS and/or CIS | on-demand_Mtr-read_data req | 25 trans per 1000 mtrs per day | > 99.5% | < 30sec - < 1m
94 | 1Ab, 1B, 7 |  | Meter reading | Head End shall be able to report on request read commnication failure to the mdms MDMS and/or Network Management System [new actor] and/or CIS | on-demand_Mtr-read_data_comm_fail rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s
95 | 1Ab, 1B, 7 |  | Meter reading | Head End shall be able to report meter read errors to the MDMS and/or Network Management System [new actor] and/or CIS | on-demand_Mtr-read_data_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 10s
96 | 1C |  | Meter reading | Head End shall be able to obtain multiple Smart Meter's data from the DAP on a configurable schedule | bulk_Mtr-read_data rpns | 4-6 bulk meter read operations per day | > 99.5% | < 1hr |  |  | This seems to assume that DAPs are data storage devices in the field and that meter reads are architeced as Pulls from the Head end versus other PUSH from the meter technologies and DAPS are only temporary data sorage queues/data buffers. Far more meter data is retained (measured in scores of days) than a few days at best for DAPs
97 | 1B, 1C, 1D |  | Meter reading | Head End shall be able to report multiple Smart Meter's data via Smart Meter PUSH or Head-End PULL on a configurable schedules to MDMS | bulk_Mtr-read_data rpns | 4-6 bulk meter read operations per day | > 99.5% | < 1hr
98 | 1C, 1D |  | Service Switch | Head End shall be able to send change service switch state to Smart Meters | SW_opr req | 1-50 trans per 1000 mtrs per day | > 99% | < 15m
99 | 1C, 1D |  | Service Switch | Head End shall be able to send request service switch status to Smart Meters | SW_status req | 1-50 trans per 1000 mtrs per day | > 99% | < 15m
100 | 1B, 7 |  | Service Switch | Head end shall be able to report communication failure with the desired device [what's the desired device?] | head-end_comm_fail rpns | 1-4 trans per 1000 mtrs per day | > 99% | < 15m
101 | 9 |  | PHEV | Head End shall be able to notifiy the LMS of communication failures with re-charging rate communication | PHEV_chrg_rate_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 15m
102 | 8 |  | PHEV | Head End shall be able to notifiy the DSM of communication failures with price communication | PHEV_price_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 15m
103 | 1B |  | PHEV | Head End shall be able to notifiy the MDMS of communication failures with VIN numbers transactions [is PHEV Vin info only stored in MDMS or in someother actor e.g. CIS?] | PHEV_Vin_data_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 15m
104 | 1C, 1D, 5Bb, 5Bc |  | PHEV | Head End shall be able to notify the ESI of Re-Charging rate communication failures with the LMS | PHEV_chrg_rate_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 15m
105 | 1C, 1D, 5Bb, 5Bc |  | PHEV | Head End shall be able to notify the ESI of price communication failures with the DMS | PHEV_price_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 15m
106 | 1C, 1D, 5Bb, 5Bc |  | PHEV | Head End shall be able to notify the ESI of VIN communication failures with the MDMS | PHEV_Vin_data_comm_fail rpns | 1 trans per 1000 mtrs per day | > 99.5% | < 10s
107 | 9 |  | PHEV | Head End shall be able to publish agreed upon re-charging rate to the LMS | PHEV_chrg_rate rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s
108 | 9 |  | PHEV | Head End shall be able to publish PHEV charging status to the LMS | PHEV_chrg_status rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s
109 | 1B |  | PHEV | Head End shall be able to publish VIN information to the MDMS [is PHEV Vin info only stored in MDMS or in someother actor e.g. CIS?] | PHEV_Vin_data rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s
110 | 1C, 1D, 5Bb, 5Bc |  | Load MGMT | Shall be able to send (reliable?) multicast or unicast load control messages | load_cntrl_msg req | Broadcast trans to all enrolled DR/Load management mtrs | > 98% | < 15m
111 | 1C, 1D |  | Load MGMT | Shall be able to receive verification of control [what types and what's their individual reporting time window?] messages | load_cntrl_msg ack | 1 trans per enrolled meter | > 98% | < 30sec - < 1hr
112 | 9 |  | Load MGMT | Shall be able to send acknowledgement messages to the LMS | load_cntrl_msg ack | 1 trans per enrolled meter | > 98% | < 1h - < 4h
113 | 9 |  | Load MGMT | Shall be able to report opt-out messages to the LMS in a configurable mannor | load_cntrl_msg_optout rpns | 1 trans per 50 enrolled meter | > 98% | < 1m
114 | 1C, 1D |  | Pre-Pay | Head End shall be able to send Meter read requests to Smart Meter | on-demand_Mtr-read_data req | 25 trans per 1000 mtrs per day | > 98% | < 10s
115 | 1Ab, 1B, 1C, 1D, 10 |  | Pre-Pay | Head End shall be able to receive, process & forward Smart Meter read responses to MDMS and/or DMS and/or CIS | on-demand_Mtr-read_data rpns: bulk_Mtr-read_data rpns | 25 trans per 1000 mtrs per day | > 99.5% | < 10s - < 1h
116 | 1C, 1D |  | Pre-Pay | Head End shall be able to process/send Smart Meter switch open/close operate request to Smart Meter | SW_opr req | 1-50 trans per 1000 mtrs per day | > 98% | < 10s - < 30s
117 | 1C, 1D |  | Pre-Pay | Head End shall be able to process & send Smart Meter switch state requests to Smart Meter | SW_status req | 1-50 trans per 1000 mtrs per day | > 98% | < 10s
118 | 1C, 1D |  | Pre-Pay | Head End shall precess & send to HID Prepay messages via Smart Meter or DAP | prepay_msg_[1-10] | 25-250 trans per 1000 mtrs per day | > 98% | < 10s - < 5m
119
120 |  |  |  | Assumption: DAP could store and forward, act as an access point or route
DAP
122 | 1D |  | Meter reading | DAP shall be able to forward on demand read request from the Head End to the Smart Meter | on-demand_Mtr-read_data req | 25 trans per 1000 mtrs per day | > 99.5% | <5s
123 | 1C |  | Meter reading | DAP shall be able to forward on demand read response from Smart Meter to Head End | on-demand_Mtr-read_data rpns | 25 trans per 1000 mtrs per day | > 98% | <5s
124 | 1C |  | Meter reading | DAP shall be able to report on demand communication failure [from what device(s)] to the Head End |  | 5 trans per 1000 mtrs per day | > 99.5% | <5s
125 | 1C |  | Meter reading | DAP shall be able to forward scheduled Smart Meter data reports to the Head End | bulk_Mtr-read_data rpns | All mtrs report 4-6 times per day | 90% success every 4-6 hours 98% success over a day > 99.5% over two days | < 4hr
126 | 1C, 1D |  | Service Switch | DAP shall be able to forward on change service switch state request from the Head End to the Smart Meter | SW_opr req | 1-50 trans per 1000 mtrs per day | > 99.5% | <5s
127 | 1C |  | Service Switch | DAP shall be able to report communication failure with the next lower network layer to Head End | DAP_downstream_comm_fail rpns | 1-50 trans per 1000 mtrs per day | > 99.5% | <5s
128 | 1C, 1D, 5Bb |  | PHEV | DAP shall be able to notifiy the Head End of communication failures with PHEV re-charging rate communication | PHEV_chrg_rate_comm_fail rpns | 20 trans per 1000 mtrs | 98% | <10s
129 | 1C, 1D, 5Bb |  | PHEV | DAP shall be able to notifiy the Head End of communication failures with PHEV price communication | PHEV_price_comm_fail rpns | 20 trans per 1000 mtrs | 98% | <10s
130 | 1C, 1D, 5Bb |  | PHEV | DAP shall be able to notifiy the Head End of communication failures with PHEV VIN numbers transactions | PHEV_Vin_data_comm_fail rpns | 20 trans per 1000 mtrs | 98% | <10s
131 | 1D, 5Bb |  | PHEV | DAP shall be able to notify the Smart Meter ESI of PHEV Re-Charging rate communication failures with the Head End | PHEV_chrg_rate_comm_fail rpns | 1 trans per 1000 mtrs | 99.5% | <10s
132 | 1D, 5Bb |  | PHEV | DAP shall be able to notify the Smart Meter ESI of PHEV price communication failures with the Head End | PHEV_price_comm_fail rpns | 1 trans per 1000 mtrs | 99.5% | <10s
133 | 1D, 5Bb |  | PHEV | DAP shall be able to notify the Smart Meter ESI of PHEV VIN communication failures with the Head End | PHEV_Vin_data_comm_fail rpns | 1 trans per 1000 mtrs | 99.5% | <10s
134 | 1C, 1D, 5Bb |  | PHEV | Smart Meter ESI shall be able to publish agreed upon PHEV re-charging rate(Price) to the Head End | PHEV_chrg_rate rpns | 150 trans per 1000 mtrs 2-4 times per day | 98% | <10s
135 | 1C, 1D, 5Bb |  | PHEV | Smart Meter ESI shall be able to publish PHEV charging status to the Head End | PHEV_chrg_status rpns | 150 trans per 1000 mtrs 2-4 times per day | 98% | <10s
136 | 1C, 1D, 5Bb |  | PHEV | Smart Meter ESI shall be able to publish PHEV VIN information to the Head End | PHEV_Vin_data rpns | 150 trans per 1000 mtrs 1-4 times per day | 98% | <10s |  | May change if PHEV adoption is faster or slower
137 | 1D, 5Bb |  | Load MGMT | Shall be able to send (reliable?) multicast or unicast load control messages | load_cntrl_msg req | 3-6 trans per meter per day | > 98% | <15m
138 |  |  | Load MGMT | Shall be able to receive & forward acknowledgements of successful load management request | load_cntrl_msg ack | 3-6 trans per meter per day | > 98% | <1hr
139 | 1D, 5Bb |  | Load MGMT | Shall be able to report communication failure of load control [what types and what's their individual reporting time window?] messages | load_cntrl_msg_comm_fail rpns
140 | 1C, 1D, 5Bb |  | Load MGMT | Shall be able to report opt-out messages to the Head End in a configurable mannor | load_cntrl_msg_optout rpns | 1% of mtrs per day | > 98% | < 15m
141 |  |  | Pre-Pay | DAP shall be able to forward all received Head End structured messages and commands to target Meter/Meter NIC & AMI-ESI |  | 1-3 trans per pre-pay meter per day | > 98% | < 15m |  |  | remove, replaced by the Smart meter ref in Pre-Pay item 143 below
142 |  |  | Pre-Pay | DAP shall be able to forward all received Meter/Meter NIC & AMI-ESI origianated messages |  | 1-3 trans per pre-pay meter per day | > 98% | < 15m |  |  | remove, replaced by the Smart meter ref in Pre-Pay item 144 below
143 | 1C, 1D, 5Bb |  | Pre-Pay | DAP shall be able to forward all received Head End structured messages and commands to target Smart Meter | prepay_msg_[1-10]; SW_opr req; SW_status req | 25 - 225 trans per 1000 mtrs per day | > 98% | < 1m for messages < 30s for commands
144 | 1C, 1D, 5Bb |  | Pre-Pay | DAP shall be able to forward all received Smart Meter origianated messages and commands to Head End |  | 25 - 225 trans per 1000 mtrs per day | > 98% | < 1m for messages < 30s for commands
145 | [9 empty] | Data size
|  |  |  | Smart Meter | [5 empty] | low | High
147 | 1D, 16Ba |  | Meter reading | Smart Meter shall be able send on demand read information to DAP and/or IHD via Smart Meter | on-demand_Mtr-read_data rpns | 1 trans per meter on demand | > 98% | < 5s |  | 50-100
148 | 1D, 16Ba |  | Meter reading | Smart Meter shall be able to report on demand read communication failure to DAP and/or IHD via Smart Meter | on-demand_Mtr-read_data_comm_fail rpns | 1 trans per meter on demand | > 98% | < 5s
149 | 1D |  | Meter reading | Residential Electric Smart Meter shall be able to report when meter read scheduled to DAP | Mtr-read_schd rpns | All mtrs report 4-6 times per day | > 98% | < 4hr |  | 9000
150 |  |  | Meter reading | Residential Gas Smart Meter shall be able to report when meter read scheduled to DAP | Mtr-read_schd rpns | All mtrs report 1-6 times per day | > 98% | < 4hr
151 | 1D |  | Meter reading | Commercial Electric Smart Meter shall be able to report when meter read scheduled to DAP | Mtr-read_schd rpns | Intervals of 15min to 1 hour 4-20 Data points (e.g. Voltage, Var, Register Delivered, etc.) on a push/pull period of every 1-6 hours | > 98% | < 3hr
152 |  |  | Meter reading | Commercial Gas Smart Meter shall be able to report when meter read scheduled to DAP | Mtr-read_schd rpns | All mtrs report 1-6 times per day. May have 15min intervals versus 1 hour | > 98% | < 4hr
153 | 1D |  | Service Switch | Smart Meter shall accept change service switch operations from the DAP | SW_opr req | 1-2 trans | > 98% | < 1m
154 | 1D |  | Service Switch | Smart Meter shall accept service switch status request from the DAP | SW_status req | 1-2 trans | > 98% | < 1m
155 | 1D |  | Service Switch | Smart Meter may be able to report metrology information after a successful service switch operation to DAP | SW_status rpns | 1-2 trans | > 98% | < 1m
156 | 1D |  | Service Switch | Smart Meter shall be able to report failure of service switch operation to DAP | SW_opr_fail rpns | 1-2 trans | > 98% | < 5s
157 | 1D |  | Service Switch | Smart Meter shall be able to report successful service switch operation to DAP | SW_status rpns | 1-2 trans | > 98% | <1m
158 | 16Aa |  | PHEV | Smart Meter ESI shall be able to communicate to PHEV to negotiate PHEV re-charging rates | PHEV_chrg_rate rpns | 2-4 trans per meter per day | > 98% | <10s
159 | 16Aa |  | PHEV | Smart Meter ESI shall be able to publish price information to the PHEV | PHEV_price rpns | 2-4 trans per meter per day | > 98% | <10s
160 | 1C, 1D |  | PHEV | Smart Meter ESI shall be able to forward PHEV VIN information to the Head END | PHEV_Vin_data rpns | 2-4 trans per meter per day | > 98% | <10s
161 | 16Aa |  | PHEV | Smart Meter ESI shall be able to negotiate PHEV re-charging rates with the PHEV | PHEV_chrg_rate req | 2-4 trans per meter per day | > 98% | <10s
162 | 1C, 1D |  | PHEV | Smart Meter ESI shall be able to publish agreed upon PHEV re-charging rate to the Head End | PHEV_chrg_rate rpns | 2-4 trans per meter per day | > 98% | <10s
163 | 1C, 1D |  | PHEV | Smart Meter ESI shall be able to publish PHEV charging status to the Head End | PHEV_chrg_status rpns | 2-4 trans per meter per day | > 98% | <10s
164 | 1D |  | Load MGMT | Shall be able to receive load management requests from DAP | load_cntrl_msg req | 3-6 trans per meter per day | > 98% | <15m
165 |  |  | Load MGMT | Shall be able to acknowledge successful receipt of load management messages from DAP | load_cntrl_msg ack | 3-6 trans per meter per day | > 98% | <1hr
166 | 1D |  | Load MGMT | Shall be able to report opt-out messages to the DAP in a configurable mannor | load_cntrl_msg_optout rpns | 1-2 trans per meter per day | > 98% | <1m
167 | 16Ba, 16Bb |  | Pre-Pay | ESI shall be able to process & forward messages received from Smart Meter and/or 3rd party broadband to IHD | prepay_msg_[1-10] | 1-10 trans per day | > 99% | <5s
168 | 16Ba, 16Bb |  | Pre-Pay | ESI shall be able to process & forward IHD messages and proxied command requests upstream to Smart Meter and/or 3rd party broadband | prepay_IHD_msg rpns; prepay_IHD_cmds req | 1-10 trans per day | > 98% | < 5s
169 | 5Bb, 16Ba, 16Bb |  | Pre-Pay | ESI may receive/send messages with AMI network interface point [Smart Meter or networked field device] | prepay_msg_[1-10] | 1-10 trans per day | > 98% | < 5s
170 |  |  | Pre-Pay | ESI may receive/send messages with Meter/Meter NIC |  | 1-10 trans per day | > 98% | < 5s |  |  | remove, this is at too detailed level
171 |  |  | Pre-Pay | Meter SW shall be able to open/close upon receipt of signal from Meter |  | 1-10 trans per day | > 98% | < 5s
172 |  |  | Pre-Pay | Meter shall be able to process received messages & commands |  | 1-10 trans per day | > 98% | < 5s
173 |  |  | Pre-Pay | Meter may be able to send messages & command responses to connected AMI-ESI |  | 1-10 trans per day | > 98% | < 5s |  |  | remove, this is at too detailed level
174 |  |  | Pre-Pay | Meter shall be able to process & send open/close signal to Meter SW |  | 1-10 trans per day | > 98% | < 5s |  |  | remove, this is at too detailed level
175 | 1D |  | Pre-Pay | Smart Meter shall be able to process & send switch state to DAP |  | 1-10 trans per day | > 98% | < 5s
176
ESI without AMI system backhaul
178 | 2G, 5Bc |  | PHEV | ESI shall be able to communicate with LMS to negotiate re-charging rates | PHEV_chrg_rate req | 2-4 trans per day | > 99% | <10s
179 | 16Ab |  | PHEV | ESI shall be able to publish price information to the PHEV | PHEV_price rpns | 2-4 trans per day | > 99% | <10s
180 | 2G, 5Bc |  | PHEV | ESI shall be able to forward PHEV VIN information to the MDMS | PHEV_Vin_data rpns | 2-4 trans per day | > 99% | <10s
181 | 16Ab |  | PHEV | ESI shall be able to negotiate re-charging rates with the PHEV | PHEV_chrg_rate req | 2-4 trans per day | > 99% | <10s
182 | 2G, 5Bc |  | PHEV | ESI shall be able to publish agreed upon re-charging rate to the LMS | PHEV_chrg_rate rpns | 2-4 trans per day | > 99% | <10s
183 | 2G, 5Bc |  | PHEV | ESI shall be able to publish PHEV charging status to the LMS | PHEV_chrg_status rpns | 2-4 trans per day | > 99% | <10s
184 | 16Bb |  | Pre-Pay | 3rd party ESI shall be able to process & forward messages to IHD | prepay_msg_[1-10] | 1-10 trans per day | > 99% | < 5s
185 | 16Bb |  | Pre-Pay | 3rd party ESI shall be able to process & forward IHD messages and proxied command requests uptream | prepay_IHD_msg rpns; prepay_IHD_cmds req | 1-10 trans per day | > 99% | < 5s
186 |  |  | Pre-Pay | ESI may receive/send messages with AMI network interface point |  | 1-10 trans per day | > 99% | < 5s |  |  | remove, does not apply to this use case
187 | 5Bc |  | Pre-Pay | 3rd party ESI shall receive/send messages with broadband 3rd prty broadband connection point |  | 1-10 trans per day | > 99% | < 5s
188
PHEV
190 | 16Aa, 16Ab |  | PHEV | PHEV shall be able to communicate with the ESI |  | 2-4 trans per day | > 99% | <10s
191 | 16Aa, 16Ab |  | PHEV | PHEV shall be able to accept price information from the ESI | PHEV_price rpns | 2-4 trans per day | > 99% | <10s
192 | 16Aa, 16Ab |  | PHEV | PHEV shall be able to negotiate re-charging rate with the ESI | PHEV_chrg_rate req | 2-4 trans per day | > 99% | <10s
193 | 16Aa, 16Ab |  | PHEV | PHEV shall be able to publish charging status of the PHEV to the ESI | PHEV_chrg_status rpns | 2-4 trans per day | > 99% | <10s
194
Phone
196 |  |  | Pre-Pay | Phone shall be able to receive automated voice Prepay messages | prepay_msg_[1-10] | 1-10 trans per day | > 99% | <5s
197
SMS Text Device
199 |  |  | Pre-Pay | SMS Text Device shall be able to receive & display Prepay messages | prepay_msg_[1-10] | 1-10 trans per day | > 99% | < 5s
200
IHD
202 | 16Ba, 16Bb |  | Pre-Pay | IHD shall be able to process, display received Prepay messages from ESI | prepay_msg_[1-10] | 1-10 trans per day | > 99% | < 5s
203 | 16Ba |  | Pre-Pay | IHD shall be able to request Meter readings & shall be able to request on-demand Meter readings via Smart Meter | on-demand_Mtr-read_data req | 1-10 trans per day | > 99% | < 5s
204 | 16Bb |  | Pre-Pay | IHD shall be able to request Meter readings & shall be able to request on-demand Meter readings [via Utility] via 3rd party broadband ESI | on-demand_Mtr-read_data req: bulk_Mtr-read_data req | 1-10 trans per day | > 99% | < 5s - < 5m