UCAIug: SG Net SRS

Smart Grid Networks System Requirements Specification

Release Candidate 3 revision *

DRAFT

Tuesday, July 13, 2010

Table of Contents

Document History	5

1	Overview	6

1.1	Executive Summary	6

1.1.1	Background - Energy Independence and Security Act of 2007	6

1.1.2	Priority Action Plans	6

1.1.3	Deliverables	7

1.1.4	Authors	8

1.1.5	Acknowledgements	8

1.2	Approach	8

1.2.1	SG-Network Requirements Gathering Process	8

1.2.2	System Requirement Specifications	13

1.2.3	Network and Systems Management	13

1.3	Terms and Definitions	13

2	Architecture Overview	13

3	Use Cases and Communications Requirements	31

3.1	Overview and Context	31

3.2	Distribution Automation and Intelligence Business Process Use Cases	31

3.2.1	Overview of Business Processes	31

3.2.2	Business Process Definitions	32

3.2.3	Actors	32

3.2.4	Payload Reference – PLACEHOLDER	33

3.2.5	Automated Feeder / Re-closer Switching	33

3.2.6	Voltage Regulator	36

3.2.7	Capacitor Bank Control	38

3.2.8	Fault Current Indicator	39

3.2.9	Transformer Monitoring	40

3.2.10	Voltage and Current Sensors	42

3.2.11	Network Protection Monitoring	43

3.2.12	Throw Over Switch Monitoring	44

3.2.13	Health Checks	46

3.2.14	Distribution Automation Network Design and Provisioning	46

3.3	Metering and Metering Events Business Processes Use Cases	49

3.3.1	Overview of Business Processes	49

3.4	PHEV Use Cases	55

3.4.1	Objectives	55

3.4.2	Actors	55

3.4.3	Latency Requirements	55

3.4.4	Process Flow	55

3.4.5	Included Processes	55

List of Tables

Table 1- Pertinent Use Cases	10

Table 2 - Actors	10

Table 3 - Actor Domain Mapping	11

Table 4 - Smart Grid Functional & Volumetric Business Requirements	16

Table 5 - Distribution Automation Actor Descriptions	33

Table 6 - Actors Automated Feeder Switching	33

Table 7 - Applicable Distribution Applications	33

Table 8 - Latency requirements AFS operation	34

Table 9 - Latency requirements Automated Feeder Switch Telemetry	34

Table 10 - Actors Voltage Regulator Operation	36

Table 11 - Applicable Distribution Applications	36

Table 12 - Latency requirements Voltage Regulator Operation	36

Table 13 - Latency requirements Voltage Regulator Telemetry	37

Table 14 - Actors Capacitor Banks	37

Table 15 - Applicable Distribution Applications	38

Table 16 - Latency requirements Capacitor Bank Operation	38

Table 17 - Actors Fault Current Indicator	39

Table 18 - Applicable Distribution Applications	39

Table 19 - Latency requirements Fault Current Indicator	40

Table 20 - Actors Transformer Monitoring	40

Table 21 - Applicable Distribution Applications	41

Table 22 – Latency requirements Transformer Monitoring	41

Table 23 - Actors Voltage and Current Sensors	42

Table 24 - Applicable Distribution Applications	42

Table 25 -Latency requirements Amp / voltage sensor	42

Table 26 - Actors Network Protector Monitoring	43

Table 27 - Applicable Distribution Applications	44

Table 28 - Latency Requirements Network Protector Monitoring	44

Table 29 - Actors Throw Over Switch Monitoring	44

Table 30 - Applicable Distribution Applications	45

Table 31 - Latency Requirements Throw Over Switch Monitoring	45

Table 32 – Actors Device Health Check	46

Table 33 - Latency Requirements Device Health Check	46

Table 34 - Actors Distribution Logical Network Design	47

Table 36 – Meter Reading Actors	49

Table 37 – Outage Notification Actors	50

Table 38 – Electric Service Prepayment Actors	51

Table 39 - Metering Audit Event Actors	52

Table 40 - Metering Configuration Event Actors	53

Table 41 - Metering Fault Alarm Actors	53

Table 42 - Metering Power Quality Actors	54

Table 43 - Metering Security Event Actors	55

List of Figures

Figure 1 - Open SG structure	7

Figure 2 - Baseline Diagram Without Cross Domain & Network	14

Figure 3 - Baseline Diagram with Cross Domain & Network flows	15

Figure 4 - Customer Information / Messaging Use Case	17

Figure 5 - Distribution Automation Use Case	18

Figure 6 - Meter Read Use Case	19

Figure 7 - PHEV Use Case	20

Figure 8– PrePay Use Case	21

Figure 9 - Service Switch	23

Figure 10 – Utility CIS <-> Meter Communication Path Scenarios	24

Figure 11– IPD & Customer. EMS <-> Meter Communication Path Scenarios	25

Figure 12 - Web Portal <-> ODS Communication Path Scenarios	26

Figure 13 – Utility CIS <-> IPD Communication Path Scenarios	27

Figure 14 – REP CIS <-> IPD Communication Path Scenarios	28

Figure 15 – DMS <-> DA Feeder Devices Communication Path Scenarios	29

Figure 16– DMS <-> DA Substation Devices Communication Path Scenarios	30

Figure 17 - Information flow AFS automated operation	34

Figure 18 - Information flow AFS Manual Switch Operation	34

Figure 19 - Information flow AFS monitoring and diagnostics	35

Figure 20 - Information flow AFS manual DNP configuration change	35

Figure 21 - Information flow manual switch operation and DNP configuration change	35

Figure 22 - Information flow Voltage Regulator operation	37

Figure 23 - Information flow Capacitor Bank Control	38

Figure 24 - Information flow Capacitor Bank Monitoring	39

Figure 25 - Information flow Fault current Indicator	40

Figure 26 - Information flow Transformer Monitor	41

Figure 27 - Information flow Amp / Voltage Sensor	42

Figure 28 - Information flow Network Protector	44

Figure 29 - Information flow Throw Over Switch	45

Figure 30 - Information flow Health check	46

Figure 31 - Process flow Distribution Logical Network Design	47

# Document History

Revision History

| Revision Number | Revision Date | Revision By | Summary of Changes | Changes marked |
| --- | --- | --- | --- | --- |
| 1.01 |  |  | Documented shell created | N |
| 1.02 | 2/16/10 | MKG | Result from 2/16/10 conference call | N |
| 1.03 | 2/16/10 | Armes/MKG | Cleaned up definitions and acronyms | N |
| 1.04 | 2/16/10 | MKG | Added TOC and Draft Preface | N |
| 1.05 | 2/22/10 | MKG | Added Requirements specification info | N |
| 1.06 | 2/22/10 | MKG | Clerical updates to links to work | N |
| 2 | 2/22/10 | MKG | Updated version number for release | N |
| 3 rc1 | 4/17/10 | MKG/RTC | Updated Use case flow charts and diagrams | N |
| 3 rc3 | 4/17/10 | RTC | Added links to documentation instructions | Y |
| 3 rc5 | 4/18/10 | MKG | Added acknowledgements and minor edits. Made images/illustrations portrait versus landscape | N |
| 3rc6 | 6/1/2010 | GC | Harmonized use case document with original RC3 | N |
| 3RCx | 6/7/10 | GC | Updating Use Case descriptions and nomenclature | N |

# Overview

## Executive Summary

### Background - Energy Independence and Security Act of 2007

Under the Energy Independence and Security Act (EISA) of 2007, the National Institute of Standards and Technology (NIST) is assigned “primary responsibility to coordinate development of a framework that includes protocols and model standards for information management to achieve interoperability of Smart Grid devices and systems…” [EISA Title XIII, Section 1305]. There is an urgent need to establish these standards. Deployment of various Smart Grid elements, such as smart meters, is already underway and will be accelerated as a result of Department of Energy (DOE) Investment Grants. Without standards, there is the potential for these investments to become prematurely obsolete or to be implemented without necessary measures to ensure security.

Recognizing the urgency, NIST developed a three-phase plan to accelerate the identification of standards while establishing a robust framework for the longer-term evolution of the standards and establishment of testing and certification procedures.

### Priority Action Plans

PAPs arise from the analysis of the applicability of Standards to the Use Cases of the Smart Grid. PAPs include identified experts in relative SDOs, known as the PAP Working Group Management Team.

Specifically, a PAP addresses either:

A gap where a standard or standard extension is needed:

- The need for meter image-download requirements is an example of a non-existing standard needed to fill an identified gap.

An overlap where two complementary standards address some information that is in common but different for the same scope of an Application:

- An example of this is metering information where CIM, 61850, ANSI C12.19, SEP 1&2 all have non-equivalent methods of representing revenue meter readings.

### Deliverables

This document has been created to support NIST Smart Grid Interoperability Priority Action Plans (PAP) 1 & 2 and provide Utilities, Vendors and Standard Development Organizations a system requirements specification for Smart Grid Communication.

For PAP 1 the tasks assigned to UCAiug (SG-Network) are as follows:

Task 1: Develop a set of requirements for different Smart Grid applications

For PAP 2 the tasks assigned to UCAiug (SG Network) are as follows:

Task 1: Segment the smart grid and wireless environments into a minimal set of categories for which individual wireless requirements can be identified.

Task 3: Compile & communicate use cases and develop requirements for all smart grid domains in terms that all parties can understand.

Task 4: Compile and communicate a list of capabilities, performance metrics, etc. in a way that all parties can understand. - Not quantifying any standard, just defining the set of metrics.

To accomplish these assignments, the UCAiug Open Smart Grid (OpenSG) has assigned these tasks to a task force within the SG Communications working group called SG Network to formally work on these tasks.

Figure 1 - Open SG structure

### Authors

The following individuals and their companies are members of the OpenSG SG-Network Task Force Core Development Team and contributed substantially to the drafting of the SG-Network System Requirement Specification:

Jerry Armes, Micronet Communications

Vincent Bemmel, Trilliant

John Buffington, Itron

George Cosio, Florida Power & Light, Co.

Ron Cunningham, American Electric Power

Paul Duffy, Cisco Systems

Kelly Flowers, Detroit Edison

Matt Gillmore, Consumers Energy

Bill Godwin, Progress Energy

Bill Leslie, Longboard Technologies

Claudio Lima, Sonoma Innovations

Michael Northern, Deloitte Consulting LLP

David Pilon, Detroit Edison

Gary Stuebing, Duke Energy

Don Sturek, Pacific Gas & Electric

### Acknowledgements

The content delivered by the SG-Network task force would not be possible without feedback and consensus from the overall industry.  Listed below are individuals who have provided substantial feedback and guidance to SG-Network.

David Cypher, NIST

Nada Golmie, NIST

Erich Gunther, Enernex

Pat Kinney, Kinney Consulting

Mark Kleerer, Qualcomm

Bruce Kraemer, Marvell

Wayne Longcore, Consumers Energy

Geoff Mulligan, IPSO Alliance

Robby Simpson, GE Energy

Phil Slack, Florida Power & Light, Co.

David Su, NIST

## Approach

### SG-Network Requirements Gathering Process

The SG-Network task force derived functional requirements from the following process:

- Listing of pertinent use cases

- Identification of Actors within use cases

- Gap analysis by mapping actors to use cases

- Defining Business Functional and Volumetric Requirements

  - Requirement actor to actor

  - Estimated payload

  - Expected latency

  - Expected Reliability

  - Security Requirements

    - Low, Medium, High per NISTIR 7628

  - Implications of failure

- Smart Grid Domain, Actor, Interface reference diagram

  - Illustrative diagram of requirements

#### Listing of pertinent use cases

In order to create a list of functional requirements for the Smart Grid, an exercise was performed to list all pertinent use cases that involve network communication.  Sources for this information include the Southern California Edison Use Cases, Grid Wise Architectural Console use cases, EPRI and others.  Use cases from all of these sources were selected based upon a network requirements basis.  From this research the following high level use cases have been identified.

| Smart Grid Use Case | Requirements Derived | Requirements included in release 4.0 and later |
| --- | --- | --- |
| Meter Read | Yes | Yes |
| Direct load control | In progress | No |
| Service Switch | Yes | Yes |
| PHEV | Yes | Yes |
| System updates | In progress | No |
| Distributed GEN | In progress | No |
| Distributed Storage | Draft | No |
| Outage Events | Yes | Yes |
| Tamper Events | Draft | No |
| Meter Events | Draft | No |
| Demand Response | Draft | No |
| Pre-Pay Metering | Yes | Yes |
| Field Force tools | Not started | No |
| Distribution automation support | Yes | Yes |
| Transmission automation support | Not started | No |
| Pricing TOU / RTP/ CPP | in progress | No |
| Configuration mgmt | in progress | No |
| Accounting Mgmt | in progress | No |
| Performance Mgmt | in progress | No |
| Security mgmt | in progress | No |
| Fault mgmt | in progress | No |
| Volt/VAR Management | Yes | Yes |

Table 1- Pertinent Use Cases

The “Requirements Derived” Column of the above table shows that requirements have been produced for the use case.  However the requirements will not be submitted for wider audiences until they have been fully vetted.  Requirements that are fully vetted have a “Yes” in the “Requirements Fully Vetted” column.

#### Identification of Actors within Use Cases

After the use cases were identified.  Members of SG Network reviewed the existing use cases from the industry and defined the actors.  While doing this exercise the actors were also added to architectural domains:

| Actor | Domain |
| --- | --- |
| Meter Data Management System | Operations |
| Asset Management System | Operations |
| Energy Management System | Operations |
| Demand Side Management System | Operations |
| Event / OMS System | Operations |
| Distribution Management System | Operations |
| Load Management System | Operations |
| Supervisory Control and Data Acquisition System | Operations |
| Geospatial Information System | Operations |
| Network Management System | Operations |
| Head End System | Operations |
| Capacitor Bank | Distribution |
| Voltage Regulator | Distribution |
| Meduim Voltage Sensor | Distribution |
| Recloser Teamed | Distribution |
| Recloser Not Teamed | Distribution |
| Phase Measuring Unit | Distribution |
| Fault Detector | Distribution |
| Data Aggregation Point | Transmission and Distribution |
| Smart Meter | Customer |
| Energy Services Interface | Customer |
| In Home Display | Customer |
| Customer Information System | Service Provider |
| Customer Information System 3rd Party | Service Provider |

Table 2 - Actors

#### Gap analysis by mapping actors to use cases

Having collected a list of actors and use cases, the gab analysis was conducted by mapping actors to use cases.  The exercise involved a review of each selected use case and mapping which actors apply.  Below is an example of this process for Meter Reading.

| Actor | Domain | Use Case: Meter Reading |
| --- | --- | --- |
| Meter Data Management System | Operations | Yes |
| Asset Management System | Operations | No |
| Energy Management System | Operations | No |
| Demand Side Management System | Operations | No |
| Event / OMS System | Operations | No |
| Distribution Management System | Operations | No |
| Load Management System | Operations | No |
| Supervisory Control and Data Acquisition System | Operations | No |
| Geospatial Information System | Operations | No |
| Network Management System | Operations | No |
| Head End System | Operations | Yes |
| Capacitor Bank | Distribution | No |
| Voltage Regulator | Distribution | No |
| Medium Voltage Sensor | Distribution | No |
| Recloser Teamed | Distribution | No |
| Recloser Not Teamed | Distribution | No |
| Phase Measuring Unit | Distribution | No |
| Fault Detector | Distribution | No |
| Data Aggregation Point | Transmission and Distribution | Yes |
| Smart Meter | Customer | Yes |
| Energy Services Interface | Customer | Yes |
| In Home Display | Customer | Yes |
| Customer Information System | Service Provider | Yes |
| Customer Information System 3rd Party | Service Provider | Yes |

Table 3 - Actor Domain Mapping

#### Defining Business Functional and Volumetric Requirements

The process of requirements gathering has been evolutionary in nature.  The SG Network task force has defined over 1400 (as of release 4.0) functional requirements while reviewing the use cases identified previously.  The group intends to release versions of requirements over time in order to keep scope and focus attainable yet giving consumers of this information something to work with and provide feed back.

The requirements have been captured in a spreadsheet that matches the version of this document.  A partial description of the spreadsheet and its columns are below. For a more complete description, refer to the latest version of the “Requirements Documentation Instructions” located in the SG-Network Task Force webpage folder .

Spreadsheet Column Descriptions

- Rqmt Ref – This column is a reference to the original worksheet line number the requirement originally defined

- Data-Flow Ref – This column is a reference to the architectural reference models lines between actors shown illustratively in this document and attached to this work as a separate file

- Data Flow From Actor – This column indicates the actor that is considered the sender of information noted in the Requirements Column

- Data Flow to Actor – This column indicates the actor that is considered the desired recipient of the information noted in the Requirements Column

- Requirements – This column is the actual application requirement.  Words like “shall” in this column are to be considered required, while words like “may” should be considered optional

- Payload Name – This column explains the scenario type of the requirement derived from the use case. (e.g. Bulk, On Demand for meter reading)

- Candidate NIST LIC – NISTIR 7628 document values used in establishing values

- Security Confidentiality – NISTIR 7628 document values used in establishing values

- Security Integrity – NISTIR 7628 document values used in establishing values

- Security Availability – NISTIR 7628 document values used in establishing values

- Latency - Summation of the node processing time and network time for a specific pairing of actors from the “from” actor to the “to” actor, excluding communications and protocol or security overheads.

- Reliability - The probability that an operation will complete without failure over a specific period or amount of time.

- Payload Size Type – This column indicates whether the payload is native (encoded in a compact format), intgrt (encoded in an API or web service format) or Display (encoded in a format for a user interface)

- App Payload Size – This column is an estimation of how many bytes are needed for the requirement as actual payload.

- Implications – This column is an attempt to explain the impacts of the requirements not being met for the operator of the system.

### System Requirement Specifications

### Network and Systems Management

In the development of Smart Grid related requirements and standards, it became evident that a model for managing very large communication networks did not exist.  As part of the SG Network Systems Requirements Specification the SG Network WG developed a set of common network management requirements based on the FCAPS model of network management.

FCAPS is the ISO Telecommunications Management Network model and framework for network management. FCAPS is an acronym for Fault, Configuration, Accounting, Performance, Security, the management categories into which the ISO model defines network management tasks.

## Terms and Definitions

The use of a common vocabulary has been of critical important in the development of this and other Smart Grid related work products.  All pertinent terms and definitions utilized in this document are listed in the appendix of this document.

# Architecture Overview

In these section a few illustrative diagrams are included to help the reader of this document to understand the content.  These files are also available for reference at the following locations:

The reference model diagrams locations are in the SG-Network TF webpage folder:

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Interium_Release_3/Diagrams

The SG-Network functional requirements table location is:

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Interium_Release_3/SG-Net_TF_%20funct-volumteric-reqs_v3.xls

Figure 2 - Baseline Diagram Without Cross Domain & Network

Figure 3 - Baseline Diagram with Cross Domain & Network flows

Table 4 - Smart Grid Functional & Volumetric Business Requirements

Figure 4 - Customer Information / Messaging Use Case

Figure 5 - Distribution Automation Use Case

Figure 6 - Meter Read Use Case

Figure 7 - PHEV Use Case

Figure 8– PrePay Use Case

Figure 9 - Service Switch

Figure 10 – Utility CIS <-> Meter Communication Path Scenarios

Figure 11– IPD & Customer. EMS <-> Meter Communication Path Scenarios

Figure 12 - Web Portal <-> ODS Communication Path Scenarios

Figure 13 – Utility CIS <-> IPD Communication Path Scenarios

Figure 14 – REP CIS <-> IPD Communication Path Scenarios

Figure 15 – DMS <-> DA Feeder Devices Communication Path Scenarios

Figure 16– DMS <-> DA Substation Devices Communication Path Scenarios

# Use Cases and Communications Requirements

## Overview and Context

The use cases listed in this section are intended to provide a summarization of the various use cases reviewed and analyzed by the SG Network WG.  The corresponding use case requirements listed in this document represent the most conservative requirements gathered from the utilities that participated in the SG Network WG and illustrated as reference for the worst case scenario.  In actual practice readers should establish requirements that best address the objectives of their company’s specific business case and operational requirements.

Wherever possible the use cases have been summarized in order to provide a concise account of the process, actors and requirements.  Additional information relating to the use cases is available at the SG Network Share point.

## Distribution Automation and Intelligence Business Process Use Cases

### Overview of Business Processes

The following sections outline business use cases for distribution automation.  Distribution Automation represents a fairly complex set of use cases and requirements.  The implementations of these use cases, and their accompanying requirements, will vary from utility to utility.  In addition, the implementation of distribution automation assets is not uniform across utilities.

The association of devices to specific use cases will vary across different distribution monitoring and control devices.  The author’s intent is to capture the numerous use case requirements across these monitoring and control devices.  The intent is to reflect which use cases can be applied to different distribution automation devices.

Since utility’s Distribution Automation implementations vary, the authors wished to provide a menu of different devices and use cases that could be customized to specific utility needs.

Initially we define the use cases by their respective business process.  Since Distribution Automation is a complex application, encumbering numerous applications that can be implemented in a number of ways, we have attempted to map the Distribution Automation business processes to specific distribution devices in an effort to provide an accurate depiction of the roles and uses relating different devices in a distribution network.

### Business Process Definitions

#### Maintenance

#### Voltage and Var Monitoring

#### Distribution System Demand Response DSDR

Distribution System Demand Response is an operational mode that reduced the voltage on the Distribution Grid to reduce demand (load) during periods of peak demand – with the goal of not violating any low voltage limits anywhere on the grid.

#### Line Segmentation

Line segmentation is the concept of dynamically reconfiguring loop feeders to restore the maximum number of customers after a fault has caused a section of the gird (i.e. a feeder segment) to be out of service.

#### Distributed Energy Resources

Distributed Energy Resources, also called on-site generation, dispersed generation, embedded generation, decentralized generation, decentralized energy or distributed generation, generates electricity from many small energy sources.

### Actors

| Actor | Description |
| --- | --- |
| Automated Feeder Switches | These devices are deployed at critical points with in the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system. |
| Slave | This device provides the radio communication to the Automated Feeder switch. |
| Master | This device provides radio communication between the Front End Processor, DMS and the automated feeder switch. |
| Front End Processor | This device serves as the primary conduit for issuing commands from DMS/SCADA and receiving information from field devices deployed with in the Distribution network. |
| Distribution Management System and SCADA | Application responsible for collection of distributed information and issuance of Distribution Automation commands. |
| Automated Feeder Switches | These devices are deployed at critical points with in the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system. |
| Voltage Regulators | These devices are deployed at critical points with in the Distribution network for purposes of regulating voltage and providing system telemetry regarding the performance of the electric system. |
| Capacitor Bank | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. In addition, the device can be remotely controlled in order to increase voltage on a given segment of the Distribution network. |
| Fault Current Indicator | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Transformer Monitor | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Voltage and Current sensor | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Network Protector | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Throw Over Switch | A device that provides electronic analog status and fault information. |

Table 5 - Distribution Automation Actor Descriptions

### Payload Reference – PLACEHOLDER

What is the best approach for addressing this comment from Ron?  Should we place a master payload reference for all use cases, list them with each relevant use case or simply reference them from the appendix?

### Automated Feeder / Re-closer Switching

#### Objective

The process involves the automatic isolation and notification of faults with in the Distribution electric system.  The process requires close orchestration between the DMS system and automated feeder / re-closer switching devices deployed with in the Distribution network.

#### Actors

| Actor | Role |
| --- | --- |
| Automated Feeder Switches | Primary and Secondary |
| Slave | Secondary |
| Master | Secondary |
| Front End Processor | Primary |
| Distribution Management System and SCADA | Primary |

Table 6 - Actors Automated Feeder Switching

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Recloser | Status Request | Y | Y |  |  | Y |  |
| DMS | Recloser | Sensor Data request | Y | Y |  |  | Y |  |
| DMS | Recloser | Command – Step UP | Y |  |  |  | Y |  |
| DMS | Recloser | Command – Step Down | Y |  |  |  | Y |  |
| DMS | Recloser | New Config | Y |  | Y |  | Y |  |
| Recloser | DMS | Status Change | Optional | Y |  |  |  |  |
| Recloser | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Recloser | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Recloser | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 7 - Applicable Distribution Applications

#### Latency Requirements - Switching

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| AF Switch 1 | AF Switch 2 | Event Driven | 2 Seconds | HIGH |
| AF Switch 2 | AF Switch 1 | Event Driven | 2 Seconds | HIGH |
| AF Switch 1 | Master | Event Driven | 2 Seconds | HIGH |
| AF Switch 2 | Master | Event Driven | 2 Seconds | HIGH |
| Master | AF Switch 1 | Event Driven | 2 Seconds | HIGH |
| Master | AF Switch 2 | Event Driven | 2 Seconds | HIGH |
| DMS | AF Switch 1 | Event Driven | ~5 Seconds | HIGH |
| DMS | AF Switch 2 | Event Driven | ~5 Seconds | HIGH |
| AF Switch 1 | DMS | Event Driven | ~5 Seconds | HIGH |
| AF Switch 2 | DMS | Event Driven | ~5 Seconds | HIGH |

Table 8 - Latency requirements AFS operation

#### Latency Requirements - Telemetry

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | AF Switch 1 | 5 Second Interval | ~5 Seconds | HIGH |
| DMS | AF Switch 2 | 5 Second Interval | ~5 Seconds | HIGH |

Table 9 - Latency requirements Automated Feeder Switch Telemetry

#### Process Flow

Figure 17 - Information flow AFS automated operation

#### Included Processes

##### Manual Switch Operation

Figure 18 - Information flow AFS Manual Switch Operation

##### Switch Monitoring and Diagnostics

Figure 19 - Information flow AFS monitoring and diagnostics

##### Switch Configuration Change

Figure 20 - Information flow AFS manual DNP configuration change

##### Switch Operation and Configuration Change

Figure 21 - Information flow manual switch operation and DNP configuration change

##### Switch to Switch Fault Detection

This process involves notification and interaction with devices in the event a fault is identified to have occurred in between deployed DA switches.

##### Switch to Breaker Fault Detection

This process involves notification and interaction with devices in the event a fault is identified to have occurred in between a deployed DA switch and the substation.

### Voltage Regulator

#### Objective

The process involves the automatic and manual operation of voltage regulators to improve the voltage characteristics of any particular segment of the distribution network.   The process requires close orchestration between the DMS system and voltage regulation devices deployed with in the Distribution network.

#### Actors

| Actor | Role |
| --- | --- |
| Voltage Regulators | Primary |
| Slave | Secondary |
| Master | Secondary |
| Front End Processor | Primary |
| Distribution Management System and SCADA | Primary |

Table 10 - Actors Voltage Regulator Operation

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Voltage Regulator | Status Request | Y | Y |  |  |  |  |
| DMS | Voltage Regulator | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Voltage Regulator | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Voltage Regulator | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Voltage Regulator | New Config | Y |  | Y | Y | Y | Y |
| Voltage Regulator | DMS | Status Change | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 11 - Applicable Distribution Applications

#### Latency Requirements - Operation

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | Event Driven | 5 Seconds | High |
| Voltage Regulator | DMS | Event Driven | 5 Seconds | High |
| Master | Voltage Regulator | Event Driven | 2 Seconds | High |
| Voltage Regulator | Master | Event Driven | 2 Seconds | High |

Table 12 - Latency requirements Voltage Regulator Operation

#### Latency Requirements - Telemetry

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | 5 Second Interval | ~5 Seconds | HIGH |

Table 13 - Latency requirements Voltage Regulator Telemetry

#### Process Flow

Figure 22 - Information flow Voltage Regulator operation

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Capacitor Bank Control

#### Objective

The objective is to remotely operate and poll capacitor banks for purposes of modifying the voltage and power quality on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of capacitor banks.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Capacitor Bank | Primary |

Table 14 - Actors Capacitor Banks

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Capacitor Bank | Status Request | Y | Y |  |  |  |  |
| DMS | Capacitor Bank | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Capacitor Bank | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Capacitor Bank | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Capacitor Bank | New Config | Y |  | Y | Y | Y | Y |
| Capacitor Bank | DMS | Status Change | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 15 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Capacitor Bank | Event Driven | 5 Seconds | High |
| Capacitor Bank | DMS | Event Driven | 5 Seconds | High |
| Master | Capacitor Bank | Event Driven | 2 Seconds | High |
| Capacitor Bank | Master | Event Driven | 2 Seconds | High |

Table 16 - Latency requirements Capacitor Bank Operation

#### Process Flow

Figure 23 - Information flow Capacitor Bank Control

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

##### Capacitor Bank Monitoring

Figure 24 - Information flow Capacitor Bank Monitoring

### Fault Current Indicator

#### Objective

The objective is to remotely poll and collect information from fault current indicators on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of fault current indicators.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Fault Current Indicator | Primary |

Table 17 - Actors Fault Current Indicator

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Fault Current Indicator | Status Request | Y |  |  |  | Y |  |
| DMS | Fault Current Indicator | Sensor Data request | Y |  |  |  | Y |  |
| DMS | Fault Current Indicator | New Config | Y |  |  |  | Y |  |
| Fault Current Indicator | DMS | Deviation Alert | Optional | Y |  |  | Y |  |
| Fault Current Indicator | DMS | Alarm Condition | Optional | Y |  |  | Y |  |

Table 18 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | Event Driven | 5 Seconds | High |
| Slave | DMS | Event Driven | 5 Seconds | High |
| Master | Slave | Event Driven | 2 Seconds | High |
| Slave | Master | Event Driven | 2 Seconds | High |

Table 19 - Latency requirements Fault Current Indicator

#### Process Flow

Figure 25 - Information flow Fault current Indicator

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Transformer Monitoring

#### Objective

The objective is to remotely poll and collect information from transformer monitors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of transformer monitors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Transformer Monitor | Primary |

Table 20 - Actors Transformer Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Transformer Monitor | Status Request | Y | Y |  |  |  |  |
| DMS | Transformer Monitor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Transformer Monitor | New Config | Y |  | Y | Y | Y | Y |
| Transformer Monitor | DMS | Status Change | Optional | Y |  |  |  |  |
| Transformer Monitor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Transformer Monitor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 21 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 15 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | NA | 10 Seconds | Medium |
| Master | Slave | NA | 5 Seconds | Medium |
| Slave | Master | NA | 5 Seconds | Medium |

Table 22 – Latency requirements Transformer Monitoring

#### Process Flow

Figure 26 - Information flow Transformer Monitor

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Voltage and Current Sensors

#### Objective

The objective is to remotely poll and collect information from voltage and current sensors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of voltage and current sensors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Voltage and Current sensor | Primary |

Table 23 - Actors Voltage and Current Sensors

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Sensor | Status Request | Y | Y |  |  |  |  |
| DMS | Sensor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Sensor | New Config | Y |  | Y | Y | Y | Y |
| Sensor | DMS | Status Change | Optional | Y |  |  |  |  |
| Sensor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Sensor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 24 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Second Interval | 10 Seconds | Medium |
| Slave | DMS | NA | 10 Seconds | Medium |
| Master | Slave | NA | 5 Seconds | Medium |
| Slave | Master | NA | 5 Seconds | Medium |

Table 25 -Latency requirements Amp / voltage sensor

#### Process Flow

Figure 27 - Information flow Amp / Voltage Sensor

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Network Protection Monitoring

#### Objective

The objective is to remotely poll and collect information from network protection monitors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of network protection monitors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Network Protector | Primary |

Table 26 - Actors Network Protector Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Switch | Status Request | Y | Y |  |  | Y |  |
| DMS | Switch | Sensor Data request | Y | Y |  | Y | Y |  |
| DMS | Switch | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Switch | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Switch | New Config | Y |  |  |  | Y |  |
| Switch | DMS | Status Change | Optional | Y |  |  | Y |  |
| Switch | DMS | Deviation Alert | Optional | Y |  |  | Y |  |
| Switch | DMS | Alarm Condition | Optional | Y |  |  | Y |  |
| Switch | DMS | Device Failure | Optional | Y |  |  | Y |  |

Table 27 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | Event Driven | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 28 - Latency Requirements Network Protector Monitoring

#### Process Flow

Figure 28 - Information flow Network Protector

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Throw Over Switch Monitoring

#### Objective

The objective is to remotely poll and collect information from throw over switch monitors on a particular segment of distribution.  The intent of this use case is to document the process for monitoring throw over switches.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Throw Over Switch | Primary |

Table 29 - Actors Throw Over Switch Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Switch Sensor | Status Request | Y | Y |  |  |  |  |
| DMS | Switch Sensor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Switch Sensor | New Config | Y |  | Y | Y | Y | Y |
| Switch Sensor | DMS | Status Change | Optional | Y |  |  |  |  |
| Switch Sensor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Switch Sensor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 30 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 31 - Latency Requirements Throw Over Switch Monitoring

#### Process Flow

Figure 29 - Information flow Throw Over Switch

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Health Checks

#### Objective

The objective is to remotely poll and collect information health information from distribution equipment on a particular segment of distribution.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| RTU | Primary |

Table 32 – Actors Device Health Check

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 33 - Latency Requirements Device Health Check

#### Process Flow

Figure 30 - Information flow Health check

### Distribution Automation Network Design and Provisioning

The following use cases are intended to be informational in nature.  Their inclusion in this document is to highlight the importance of some of the network management specific requirements highlighted in this document.  In the end, these use cases provide a small representation of the complex nature of Smart Grid deployments.

#### Distribution Communications Network Design

##### Objective

In order to facilitate communication between DMS, SCADA, the FEP and DA devices, each component of the solution will require the assignment of a at least one unique network address.  The address is a unique identifier for the DMS application needed to identify each device for purposes of passing control messages.  The primary goal of this process is the allocation and design of the address scheme for each logical network and all associated distribution field devices.  The result schematic will be referred to as the Distribution Logical Network Design.  Once completed the Distribution Logical Network Design serve as the reference configuration for DMS, SCADA and all other pertinent DA components.

##### Process Flow

The following diagram provides a sample process flow for development of a Distribution Logical Network Design.  The Distribution Logical Network Design involves close synchronization between Distribution devices, systems, asset management, network management and various operational systems.

Figure 31 - Process flow Distribution Logical Network Design

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Network Administrator | This is an individual responsible for operation, management and engineering of network communication infrastructure. In this process this roll will be critical in configuring the DA communication components. | Secondary |
| Distribution Engineer | The Distribution Engineer is an individual operating in a supporting role. In this process the DE provides requirements information that the Network Administrator will input into their network design for deployed communication devices. The design provided should reflect the physical and logical association between distribution assets and their respective substation. In this process the DE should develop DNP mapping tables for every device associated with a given substation. The intent is to develop the mapping of all devices with in DMS. | Primary |
| Network Management System | This application is responsible for configuring and management of network assets assigned to support DA. In this case NMS will be responsible for distributing DNP mapping tables and pertinent configuration information to all DA network components. | Primary |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. This device serves as the gateway between the DA communication devices, DMS / SCADA and NMS. | Secondary |
| Repeaters | These devices are the common communication infrastructure used for extending radio frequency coverage of a specific network. These devices may not be applicable to all DA communications architectures. | Secondary |
| Master | This device provides radio communication between the Front End Processor, DMS and the Distribution field device. These devices along with its Slave counterparts must be provisioned with DNP mapping tables that reflects the DNP configuration of all associated distribution field devices. | Secondary |
| Slave | These devices serve as the primary communications for DA field devices and must reflect the same DNP configuration as its attached RTU device. | Secondary |
| WAN | Data Aggregation Point link that provides communication between field devices and the data center. | Secondary |
| Receive Transmit Units | These are the physical DA devices attached to the Slaves. These devices along with their Master and Slave counterparts must be provisioned with DNP mapping tables. | Secondary |

Table 34 - Actors Distribution Logical Network Design

##### Included Processes

###### Documenting Geographic Location

This process involves the creation of a data file containing all relevant electronic configuration and installation location information for a given distribution automation field device.  The intent of this file is to document location specific information relating to the devices deployed in the field.  In addition, this file may serve as a reference for updating asset information in any applicable AMS.

###### Device Input into Asset Management System

This process involves updating utility asset management information in AMS as components are drawn from inventory and devices are deployed in the field.

###### Substation Distribution Logical Network and Device Input into Distribution Management System

This process involves updating device configuration information into DMS and SCADA as devices are deployed in the field.  Ideally the DMS updates should occur once a substation’s Distribution Logical Network Design is completed.  The Distribution Logical Network Design must include all assigned mapping tables for all given devices associated with a given substation. This process is intended to reflect device updates to DMS and SCADA that occur prior to the device being installed.

###### Substation Distribution Logical Network and Device Input into SCADA

This process involves updating device configuration information into SCADA as devices are deployed in the field.  Ideally the SCADA updates should occur once a substation’s DNP Logical Network Design is completed.  This process is intended to reflect device updates to DMS and SCADA that occur after the device has been installed.

###### Substation Distribution Logical Network and Device Input into NMS

This process involves updating device communications configuration information in NMS as devices are deployed in the field.  Ideally the NMS updates should occur as soon as the Distribution Logical Network Design is completed. The Distribution Logical Network Design must include all assigned device mapping tables for all given devices associated with a given substation.  In addition, the information must provide an accurate mapping between the device mapping tables, device addresses, their respective Master communications devices, Slave communication devices and their respective substation network.

## Metering and Metering Events Business Processes Use Cases

### Overview of Business Processes

#### Meter Reading

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 36 – Meter Reading Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Outage Notification

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 37 – Outage Notification Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Electric Service Prepayment

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 38 – Electric Service Prepayment Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Audit Application Event

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 39 - Metering Audit Event Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Configuration Event

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 40 - Metering Configuration Event Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Fault Error Alarm Event

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 41 - Metering Fault Alarm Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Power Quality Event

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 42 - Metering Power Quality Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

#### Security Event

##### Objective

##### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 43 - Metering Security Event Actors

##### Latency Requirements

##### Process Flow

##### Included Processes

## PHEV Use Cases

### Objectives

### Actors

### Latency Requirements

### Process Flow

### Included Processes

Appendix

Acronyms and Abbreviations

| AC | Alternating Current |
| --- | --- |
| AMI | Advanced Metering Infrastructure |
| AMS | Asset management system |
| ASAP-SG | Advanced Security Acceleration Project-Smart Grid |
| B2B | Business to Business |
| BAN | Business Area Network |
| CIM | Common Information Model. |
| CIP | Critical Infrastructure Protection |
| CSWG | Cyber Security Working Group |
| DA | Distribution Automation |
| DAP | Data Aggregation Point |
| DER | Distributed Energy Resources |
| DHS | Department of Homeland Security |
| DMS | Distribution Management System |
| DNP | Distributed Network Protocol |
| DOE | Department of Energy |
| DOMA | Distribution Operations Model and Analysis |
| DR | Demand Response |
| DSDR | Distribution Systems Demand Response |
| DSM | Demand Side Management |
| EMS | Energy Management System |
| EPRI | Electric Power Research Institute |
| ES | Electric Storage |
| ESB | Enterprise Service Bus |
| ESI | Energy Services Interface |
| ET | Electric Transportation |
| EUMD | End Use Measurement Device |
| EV/PHEV | Electric Vehicle/Plug-in Hybrid Electric Vehicles |
| EVSE | Electric Vehicle Service Element |
| FAN | Field Area Network |
| FEP | Front End Processor |
| FERC | Federal Energy Regulatory Commission |
| FIPS | Federal Information Processing Standard Document |
| FLIR | Fault Location, Isolation, Restoration |
| G&T | Generations and Transmission |
| GAPP | Generally Accepted Privacy Principles. |
| GIS | Geographic Information System |
| GPRS | General Packet Radio Service |
| HAN | Home Area Network |
| HMI | Human-Machine Interface |
| HVAC | Heating, Ventilating, and air conditioning (shown in figure) |
| I2G | Industry to Grid |
| IEC | International Electrotechnical Commission |
| IED | Intelligent Electronic Device |
| IHD | In-home Display |
| ISA | International Society of Automation |
| ISO | Independent System Operator |
| ISO/IEC27001 | International Organization for Standardization/International Electrotechnical Commission Standard 27001. |
| IT | Information Technology |
| LAN | Local Area Network |
| LMS | Load management system |
| LMS/DRMS | Load Management System/ Distribution Resource Management System |
| LV | Low voltage (in definition) |
| MDMS | Meter Data Management System |
| MFR | Multi-Feeder Reconnection |
| MSW | Meter service switch |
| MV | Medium voltage (in definition) |
| NAN | Neighborhood Area Network |
| NERC | North American Electric Reliability Corporation |
| NIPP | National Infrastructure Protection Plan |
| NIST | National Institute of Standards and Technology |
| NISTIR | NIST Interagency Report |
| NMS | Network Management system |
| OMS | Outage Management System |
| OWASP | Open Web Application Security Project |
| PAP | Priority Action Plan |
| PCT | Programmable Communicating Thermostat |
| PEV | Plug-In Electric Vehicle |
| PI | Process Information |
| PIA | Privacy Impact Assessment. . |
| PII | Personally Identifying Information |
| R&D | Research and Development |
| RTO | Regional Transmission Operator |
| RTU | Remote Terminal Unit |
| SCADA | Supervisory Control and Data Acquisition |
| SCE | Southern California Edison |
| SGIP | Smart Grid Interoperability Panel |
| SGIP-CSWG | SGIP – Cyber Security Working Group |
| SP | Special Publication |
| SSP | Sector-Specific Plans |
| T/FLA | Three/Four Letter Acronym |
| VAR | Volt-Amperes Reactive |
| VVWS | Volt-VAR-Watt System |
| WAMS | Wide-Area Measurement System |
| WAN | Wide Area Network |
| WASA | Wide Area Situational Awareness |
| WLAN | Wireless Local Area Network |
| WMS | Work Management System |

Definitions

| Actor | A generic name for devices, systems, or programs that make decisions and exchange information necessary for performing applications: smart meters, solar generators, and control systems represent examples of devices and systems. |
| --- | --- |
| Anonymize | A process of transformation or elimination of PII for purposes of sharing data |
| Aggregation | Practice of summarizing certain data and presenting it as a total without any PII identifiers |
| Aggregator | SEE FERC OPERATION MODEL |
| Applications | Tasks performed by one or more actors within a domain. |
| Asset Management System | A system(s) of record for assets managed in the Smart Grid. Management context may change(e.g. financial, network) |
| Capacitor Bank | This is a device used to add capacitance as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Common Information Model | A structured set of definitions that allows different Smart Grid domain representatives to communicate important concepts and exchange information easily and effectively. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |
| Data Collector | See Substation Controller |
| Data Aggregation Point | This device is a logical actor that represents a transition in most AMI networks between Wide Area Networks and Neighborhood Area Networks. (e.g. Collector, Cell Relay, Base Station, Access Point, etc) |
| De-identify | A form of anonymization that does not attempt to control the data once it has had PII identifiers removed, so it is at risk of re-identification. |
| Demand Side Management | A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| Distribution Management System | A system that monitors, manages and controls the electric distribution system. |
| Distribution Systems Demand Response | A system used to reduce load during peak demand. Strictly used for Distribution systems only. |
| Electric Vehicle/Plug-in Hybrid Electric Vehicles | Cars or other vehicles that draw electricity from batteries to power an electric motor. PHEVs also contain an internal combustion engine. |
| Energy Services Interface | Provides security and, often, coordination functions that enable secure interactions between relevant Home Area Network Devices and the Utility. Permits applications such as remote load control, monitoring and control of distributed generation, in-home display of customer usage, reading of non-energy meters, and integration with building management systems. Also provides auditing/logging functions that record transactions to and from Home Area Networking Devices. |
| Enterprise Service Bus | The Enterprise Service Bus consists of a software architecture used to construct integration services for complex event-driven and standards-based messaging to exchange meter or grid data. The ESB is not limited to a specific tool set rather it is a defined set of integration services. |
| Fault Detector | A device used to sense a fault condition and can be used to provide an indication of the fault. |
| Field Force | Employee working in the service territory that may be working with Smart Grid devices. |
| GAPP | Generally Accepted Privacy Principles. Privacy principles and criteria developed and updated by the AICPA and Canadian Institute of Chartered Accountants to assist organizations in the design and implementation of sound privacy practices and policies. |
| Home Area Network | A network of energy management devices, digital consumer electronics, signal-controlled or enabled appliances, and applications within a home environment that is on the home side of the electric meter. |
| Intelligent Fault Detector | A device that can sense a fault and can provide more detailed information on the nature of the fault, such as capturing an oscillography trace. |
| ISO/IEC27001 | An auditable international standard that specifies the requirements for establishing, implementing, operating, monitoring, reviewing, maintaining and improving a documented Information Security Management System within the context of the organization's overall business risks. It uses a process approach for protection of critical information |
| Last Gasp | Concept of an energized device within the Smart Grid detecting power loss and sending a broadcast message of the event. |
| Load Management System | System that controls load by sending messages directly to device (e.g. On/Off) |
| Low Voltage Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Medium Voltage Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) on a medium voltage distribution line. |
| Motorized Switch | A device under remote control that can be used to open or close a circuit. |
| Neighborhood Area Network | A network comprised of all communicating components within a distribution domain. |
| Network Management System | A system that manages Fault, Configuration, Auditing/Accounting, Performance and Security of the communication. This system is exclusive from the electrical network. |
| Outage Management System | A system that receives out power system outage notifications and correlates where the power outage occurred |
| Personal Information | Information that reveals details, either explicitly or implicitly, about a specific individual’s household dwelling or other type of premises. This is expanded beyond the normal "individual" component because there are serious privacy impacts for all individuals living in one dwelling or premise. This can include items such as energy use patterns or other types of activities. The pattern can become unique to a household or premises just as a fingerprint or DNA is unique to an individual. |
| Phase Measuring Unit | A device capable of measuring the phase of the voltage or current waveform relative to a reference. |
| Power Factor | A dimensionless quantity that relates to efficiency of the electrical delivery system for delivering real power to the load. Numerically, it is the Cosine of the phase angle between the voltage and current waveforms. The closer the power factor is to unity the better the inductive and capacitive elements of the circuit are balanced and the more efficient the system is for delivering real power to the load(s). |
| Privacy Impact Assessment | A process used to evaluate the possible privacy risks to personal information, in all forms, collected, transmitted, shared, stored, disposed of, and accessed in any other way, along with the mitigation of those risks at the beginning of and throughout the life cycle of the associated process, program or system |
| Programmable Communicating Thermostat | A device within the premise that has communication capabilities and controls heating, ventilation and cooling systems. |
| Recloser (non-Team) | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing it can be programmed to trip open and stop trying to reclose until reset either locally or under remote control. |
| Recloser (Team) | A device that can sense fault conditions on a distribution line and to communicate with other related reclosers (the team) to sectionalize the fault and provide a coordinated open/close arrangement to minimize the effect of the fault. |
| Regional Transmission Operator | A Regional Transmission Organization (RTO) is an organization that is established with the purpose of promoting efficiency and reliability in the operation and planning of the electric transmission grid and ensuring non-discrimination in the provision of electric transmission services based on the following required/demonstrable characteristics and functions. |
| Remote Terminal Unit | Aggregator of multiple serialized devices to a common communications interface |
| Sub Meter | Premise based meter used for Distributed Energy Resources and PHEV. This device may be revenue grade. |
| Substation Controller | Distributed processing device that has supervisory control or coordinates information exchanges from devices within a substation from a head end system. |
| Transformer (MV-to-LV) | A standard point of delivery transformer. In the Smart Grid context is it assumed there will be a need to measure some electrical or physical characteristics of this transformer such as voltage (high and/or low side) current, MV load, temperature, etc. |
| Use Case | Use cases are a systems engineering tool for defining a system’s behavior from the perspective of users. In effect, a use case is a story told in structure and detailed steps—scenarios for specifying required usages of a system, including how a component, subsystem, or system should respond to a request that originates elsewhere. |
| Voltage Regulator | This device is in effect an adjustable ratio transformer sitioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| VAR – Volt-Amperes Reactive; | In an AC power system the voltage and current measured at a point along the delivery system will often be out of phase with each other as a result the combined effects of the resistive and reactive (i.e. the capacitance and inductive) characteristics of the delivery system components and the load. The phase angle difference at a point along the delivery system is an indication of how well the inductive and capacitive effects are balanced at that point. The real power passing that point is the product of the magnitude of the Voltage and Current and the Cosine of the angle between the two. The VAR parameter is the product of the magnitude of the Voltage and Current and the Sine of the angle between the two. The magnitude of the VAR parameter is an indication of the phase imbalance between the voltage and current waveforms. |
| Web Portal | Interface between energy customers and the system provider. Could be the utility or third party |

# Footnotes

For additional information regarding EISA 2007,  please visit http://energy.senate.gov/public/_files/RL342941.pdf

SOURCE: NIST Smart Grid Twiki, http://collaborate.nist.gov/twiki-sggrid/bin/view/SmartGrid/PriorityActionPlans

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Interium_Release_3/

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Forms/AllItems.aspx

# Comments

What is this word supposed to be?  I took this section directly from the SRS r RC3