Smart Grid Networks System Requirements Specification

Release Candidate 3 revision *

DRAFT

Wednesday, February 29, 2012

Table of Contents

Document History	6

1	Authors	7

1.1	Acknowledgements	7

2	Overview	8

2.1	Executive Summary	8

2.1.1	Background - Energy Independence and Security Act of 2007	8

2.1.2	Goals and Objective	9

2.1.3	Priority Action Plans	10

2.1.4	Deliverables	10

2.2	Approach	12

2.2.1	SG-Network Requirements Gathering Process	12

2.3	Terms and Definitions	22

3	Illustrative Reference Architecture Overview	22

3.1.1	Alternative Paths	29

4	Use Cases and Communications Requirements	31

4.1	Overview and Context	31

4.2	Demand Response and Consumer Energy Efficiency – Matt	31

4.2.1	Demand Response	31

4.2.2	Direct Load Control	32

4.3	Energy Storage	32

4.3.1	Objectives	32

4.3.2	Actors	32

4.3.3	Latency Requirements	33

4.3.4	Process Flow	33

4.3.5	Included Processes	33

4.4	Electric Transportation	33

4.4.1	PHEV Use Cases (Vincent/Ron/Jerry)	33

4.5	System Security – Vincent / Matt	34

4.5.1	Overview – Cosio	34

4.5.2	CIA	34

4.5.3	Use Cases	34

4.5.4	Security Event (Kelly)	34

4.5.5	Audit Event (Kelly)	35

4.6	Network Communications –	36

4.6.1	Overview	36

4.6.2	Configuration Event (Ron)	36

4.6.3	Fault Error Alarm Event (Kelly)	37

4.7	Meter Reading Use Cases	39

4.7.1	Overview	39

4.7.2	Actors	41

4.7.3	Scenarios	42

Mtr-read_multi-interval-data_resp-data	44

4.8	Outage Notification	45

4.8.1	Overview	45

4.8.2	Actors	45

4.8.3	Scenarios	46

4.9	Electric Service Prepayment	46

4.9.1	Overview	46

4.9.2	Actors	46

4.9.3	Scenarios	47

4.10	Distribution Grid Management	48

4.10.1	Overview of Business Processes	48

4.10.2	Business Process Definitions	48

4.10.3	Actors	67

4.10.4	Automated Feeder / Re-closer Switching	68

4.10.5	Voltage Regulator	71

4.10.6	Capacitor Bank Control	73

4.10.7	Fault Current Indicator	74

4.10.8	Transformer Monitoring	76

4.10.9	Voltage and Current Sensors	77

4.10.10	Network Protection Monitoring	78

4.10.11	Throw Over Switch Monitoring	80

4.10.12	Health Checks	81

4.10.13	Power Quality Event (Kelly)	82

5	Appendix	84

5.1	Distribution Automation Network Design and Provisioning - (Move to appendix)	84

5.2	Acronyms and Abbreviations	87

5.3	Definitions	90

5.4	Alternative / Multiple Communication Paths	94

5.5	Application Payloads	102

List of Tables

Table 1- Pertinent Use Cases	12

Table 2 - Actors	15

Table 3 - Actor Domain Mapping	17

Table 4 - Smart Grid Functional & Volumetric Business Requirements	25

Table 5 - Actors	29

Table 6 - Actors	29

Table 7 - Actors	30

Table 8 - Actors	30

Table 9 - Metering Audit Event Actors	32

Table 10 - Metering Security Event Actors	33

Table 11 - Latency Requirements	33

Table 12 - Metering Configuration Event Actors	34

Table 13 - Latency Requirements	34

Table 14 - Metering Fault Alarm Actors	35

Table 15 - Latency Requirements	35

Table 16 – Outage Notification Actors	43

Table 17 – Outage Notification Actors	44

Table 18 - Distribution Automation Actor Descriptions	65

Table 19 - Actors Automated Feeder Switching	65

Table 20 - Applicable Distribution Applications	66

Table 21 - Latency requirements AFS operation	66

Table 22 - Latency requirements Automated Feeder Switch Telemetry	66

Table 23 - Actors Voltage Regulator Operation	68

Table 24 - Applicable Distribution Applications	69

Table 25 - Latency requirements Voltage Regulator Operation	69

Table 26 - Latency requirements Voltage Regulator Telemetry	69

Table 27 - Actors Capacitor Banks	70

Table 28 - Applicable Distribution Applications	70

Table 29 - Latency requirements Capacitor Bank Operation	71

Table 30 - Actors Fault Current Indicator	72

Table 31 - Applicable Distribution Applications	72

Table 32 - Latency requirements Fault Current Indicator	72

Table 33 - Actors Transformer Monitoring	73

Table 34 - Applicable Distribution Applications	73

Table 35 – Latency requirements Transformer Monitoring	73

Table 36 - Actors Voltage and Current Sensors	74

Table 37 - Applicable Distribution Applications	75

Table 38 -Latency requirements Amp / voltage sensor	75

Table 39 - Actors Network Protector Monitoring	76

Table 40 - Applicable Distribution Applications	76

Table 41 - Latency Requirements Network Protector Monitoring	76

Table 42 - Actors Throw Over Switch Monitoring	77

Table 43 - Applicable Distribution Applications	78

Table 44 - Latency Requirements Throw Over Switch Monitoring	78

Table 45 – Actors Device Health Check	79

Table 46 - Latency Requirements Device Health Check	79

Table 47 - Metering Power Quality Actors	79

Table 48 - Latency Requirements	80

Table 49 - Actors Distribution Logical Network Design	82

### List of Figures

Figure 2 Application Payload	16

Figure 3 - Baseline Diagram Without Cross Domain & Network	24

Figure 4 - Baseline Diagram with Cross Domain & Network flows	25

Figure 5 – Utility CIS <-> Meter Communication Path Scenarios	29

Figure 6 - Process Flow	36

Figure 7 - Process Flow	37

Figure 8 - Process Flow	38

Figure 9 - Information flow AFS automated operation	69

Figure 10 - Information flow AFS Manual Switch Operation	70

Figure 11 - Information flow AFS monitoring and diagnostics	70

Figure 12 - Information flow AFS manual DNP configuration change	70

Figure 13 - Information flow manual switch operation and DNP configuration change	71

Figure 14 - Information flow Voltage Regulator operation	72

Figure 15 - Information flow Capacitor Bank Control	74

Figure 16 - Information flow Capacitor Bank Monitoring	74

Figure 17 - Information flow Fault current Indicator	75

Figure 18 - Information flow Transformer Monitor	77

Figure 19 - Information flow Amp / Voltage Sensor	78

Figure 20 - Information flow Network Protector	80

Figure 21 - Information flow Throw Over Switch	81

Figure 22 - Information flow Health check	82

Figure 23 - Process Flow	83

Figure 24 - Process flow Distribution Logical Network Design	84

# Document History

Revision History

| Revision Number | Revision Date | Revision By | Summary of Changes | Changes marked |
| --- | --- | --- | --- | --- |
| 1.01 |  |  | Documented shell created | N |
| 1.02 | 2/16/10 | MKG | Result from 2/16/10 conference call | N |
| 1.03 | 2/16/10 | Armes/MKG | Cleaned up definitions and acronyms | N |
| 1.04 | 2/16/10 | MKG | Added TOC and Draft Preface | N |
| 1.05 | 2/22/10 | MKG | Added Requirements specification info | N |
| 1.06 | 2/22/10 | MKG | Clerical updates to links to work | N |
| 2 | 2/22/10 | MKG | Updated version number for release | N |
| 3 rc1 | 4/17/10 | MKG/RTC | Updated Use case flow charts and diagrams | N |
| 3 rc3 | 4/17/10 | RTC | Added links to documentation instructions | Y |
| 3 rc5 | 4/18/10 | MKG | Added acknowledgements and minor edits. Made images/illustrations portrait versus landscape | N |
| 3rc6 | 6/1/2010 | GC | Harmonized use case document with original RC3 | N |
| 3RCx | 6/7/10 | GC | Updating Use Case descriptions and nomenclature | N |

# Authors

The following individuals and their companies are members of the OpenSG SG-Network Task Force Core Development Team and contributed substantially to the drafting of the SG-Network System Requirement Specification:

Jerry Armes, Micronet Communications

Vincent Bemmel, Trilliant

Andrew Bordine, Consumers Energy

John Buffington, Itron

George Cosio, Florida Power & Light, Co.

Ron Cunningham, American Electric Power

Paul Duffy, Cisco Systems

Kelly Flowers, Detroit Edison

Matt Gillmore, Consumers Energy

Bill Godwin, Progress Energy

Bill Leslie, Longboard Technologies

Claudio Lima, Sonoma Innovations

Michael Northern, Deloitte Consulting LLP

David Pilon, Detroit Edison

Gary Stuebing, Duke Energy

Don Sturek, Pacific Gas & Electric

David De Yagher – BC Hydro

Cheong Siew – BC Hydro

Ed Eckert - Itron

Klaus Bender - UTC

Kory Fifield – Sensus

Mike Rodgers - Capgemini

## Acknowledgements

The content delivered by the SG-Network task force would not be possible without feedback and consensus from the overall industry.  Listed below are individuals who have provided substantial feedback and guidance to SG-Network.

David Cypher, NIST

Nada Golmie, NIST

Erich Gunther, Enernex

Pat Kinney, Kinney Consulting

Mark Kleerer, Qualcomm

Bruce Kraemer, Marvell

Wayne Longcore, Consumers Energy

Geoff Mulligan, IPSO Alliance

Robby Simpson, GE Energy

Phil Slack, Florida Power & Light, Co.

David Su, NIST

# Overview

## Executive Summary

### Background - Energy Independence and Security Act of 2007

Under the Energy Independence and Security Act (EISA) of 2007, the National Institute of Standards and Technology (NIST) is assigned “primary responsibility to coordinate development of a framework that includes protocols and model standards for information management to achieve interoperability of Smart Grid devices and systems…” [EISA Title XIII, Section 1305]. There is an urgent need to establish these standards. Deployment of various Smart Grid elements, such as smart meters, is already underway and will be accelerated as a result of Department of Energy (DOE) Investment Grants. Without standards, there is the potential for these investments to become prematurely obsolete or to be implemented without necessary measures to ensure security.

Recognizing the urgency, NIST developed a three-phase plan to accelerate the identification of standards while establishing a robust framework for the longer-term evolution of the standards and establishment of testing and certification procedures.

### Goals and Objective

The SG-Network Task force had originally started from a group called AMI-Net within the UCAiug in 2008.   With the formation of the SGIP’s Priority Action Plan process, the AMI-Net task force acquired a variety of responsibilities.

The scope of these responsibilities quickly showed a change was required in the scope and charter of the AMI-Net task force.  With these changes, the task force changed their name to SG-Network and has the following charter.

“The SG-Network task force is charged with defining functional system requirements for Management of AMI Communication systems.  The goal of this work is to identify common needs of Utilities procuring products in this space.  We anticipate utilities, academia, government and vendors to find this topic of interest and participate in this process.  This task force anticipates pulling knowledge and experience from other industries with knowledge of operating large scale networks.”

The Scope of SG-Network is as follows:

  - NIST PAP 2 (Wireless standards for the Smart Grid)

    - Supply functional requirements for Smart Grid Networks from a utility perspective

    - Define functional domains within the Smart Grid

  - Create a System Requirements Specification

  - Create a comprehensive set of non functional and functional requirements

  - Create a common reference architecture

  - Provide information to SDO’s (e.g., IEEE P2030, Zigbee Alliance, Wi-Fi, etc)

The SG-Network has endeavored to perform these tasks with the goal of having a common set of requirements, reference architecture, and having an appropriate amount of information to allow the Smart Grid Industry to build, standardize and achieve economies of scale with the products and services that they provide.

### Priority Action Plans

PAPs arise from the analysis of the applicability of Standards to the Use Cases of the Smart Grid. PAPs include identified experts in relative SDOs, known as the PAP Working Group Management Team.

Specifically, a PAP addresses either:

A gap where a standard or standard extension is needed:

- The need for meter image-download requirements is an example of a non-existing standard needed to fill an identified gap.

An overlap where two complementary standards address some information that is in common but different for the same scope of an Application:

- An example of this is metering information where CIM, 61850, ANSI C12.19, SEP 1&2 all have non-equivalent methods of representing revenue meter readings.

### Deliverables

This document has been created to support NIST Smart Grid Interoperability Priority Action Plans (PAP) 1 & 2 and provide Utilities, Vendors and Standard Development Organizations a system requirements specification for Smart Grid Communication.

For PAP 1 the tasks assigned to UCAiug (SG-Network) are as follows:

Task 1: Develop a set of requirements for different Smart Grid applications

For PAP 2 the tasks assigned to UCAiug (SG Network) are as follows:

Task 1: Segment the smart grid and wireless environments into a minimal set of categories for which individual wireless requirements can be identified.

Task 3: Compile & communicate use cases and develop requirements for all smart grid domains in terms that all parties can understand.

Task 4: Compile and communicate a list of capabilities, performance metrics, etc. in a way that all parties can understand. - Not quantifying any standard, just defining the set of metrics.

To accomplish these assignments, the UCAiug Open Smart Grid (OpenSG) has assigned these tasks to a task force within the SG Communications working group called SG Network to formally work on these tasks.

The following artifacts have been created to address the tasks described above

- System Requirements Specification (this document), including Reference Diagram and use case subsets, and Payload Attributes and Security Characteristics <MKG> add brief narrative </MKG>

- Requirements Table <MKG> add brief narrative </MKG>

- Requirements Database <MKG> add brief narrative </MKG>

## Approach

### SG-Network Requirements Gathering Process

The SG-Network task force derived functional requirements from the following process:

- Listing of pertinent use cases

- Identification of Actors within use cases

- Identification of pertinent payloads

- Gap analysis by mapping actors to use cases

- Defining Business Functional and Volumetric Requirements

  - Requirement actor to actor

  - Estimated payload

  - Expected latency

  - Expected Reliability

  - Security Requirements

    - Low, Medium, High per NISTIR 7628

  - Implications of failure

- Smart Grid Domain, Actor, Interface reference diagram

  - Illustrative diagram of requirements

#### Listing of pertinent use cases

In order to create a list of functional requirements for the Smart Grid, an exercise was performed to list all pertinent use cases that involve network communication.  Sources for this information include the Southern California Edison Use Cases, Grid Wise Architectural Console use cases, EPRI and others.  Use cases from all of these sources were selected based upon a network requirements basis.  From this research the following high level use cases have been identified.

| Smart Grid Use Case | Requirements included in release 5.0 |
| --- | --- |
| Customer Info / Messaging | Yes |
| Dispatch Distributed Customer Storage | Yes |
| Demand Response | Yes |
| Direct load control | Yes |
| Distribution System Demand Response – Centralized Control | Yes |
| Distribution System Demand Response – De-Centralized Control | No |
| Fault Clear Isolate – Distribution DAC | Yes |
| Fault Clear Isolate – Distribution Management System | Yes |
| Fault Clear Isolate – Regional Distribution DAC | Yes |
| Field Distribution Automation Maintenance – Centralized Control | Yes |
| Firmware / Program Update | Yes |
| Islanded Distribution Customer Storage | Yes |
| Meter Events | Yes |
| Meter Reading | Yes |
| Outage & Restoration Management | Yes |
| Performance Management | No |
| PHEV | Yes |
| Premises Network Administration | Yes |
| Pre-Pay Metering | Yes |
| Pricing TOU / RTP/ CPP | Yes |
| Security Management | No |
| Service Switch | Yes |
| Transmission Automation | No |
| Volt/VAR Management –Centralized | Yes |

Table 1- Pertinent Use Cases

The “Requirements Derived” Column of the above table shows that requirements have been produced for the use case.  However the requirements will not be submitted for wider audiences until they have been fully vetted.  Requirements that are fully vetted have a “Yes” in the “Requirements Fully Vetted” column.

#### Identification of Actors within Use Cases

After the use cases were identified, members of SG Network reviewed the existing use cases and reference diagrams from the industry and defined the following actors.  While doing this exercise the actors were also added to architectural domains as mapped against the SG Network TF Reference Diagram r5.0 and the Related NIST Framework and Roadmap for Interoperability Standards, Release 1.0 January 2010 – Figure 3-2 Conceptual Reference Diagram :

| SG Network TF Reference Diagram Descriptor (Actor Actor ¦ [sub Domain]) | SG Network TF Ref Diagram Primary Domain Name | Related NIST Diagram Descriptor (Actor ¦ [sub Domain]) |
| --- | --- | --- |
| Generators | Bulk Generation | Generators |
| Market Services Interface | Bulk Generation | Market Services Interface |
| Plant Control Systems | Bulk Generation | Plant Control Systems |
| DER | Customer | Electric Storage |
| Customer EMS | Customer | Customer EMS |
| DER | Customer | Distributed Generation |
| Email/Text/Web | Customer | Customer Equipment |
| ESI (3rd party) | Customer | Energy Services Interface |
| ESI (Utility) | Customer | Energy Services Interface |
| ESI (In meter) | Customer | Energy Services Interface |
| EVSE / EUMD | Customer | Customer Equipment |
| HVAC | Customer | Customer Equipment |
| IPD | Customer | Customer Equipment |
| Load Control Device | Customer | Customer Equipment |
| PCT | Customer | Thermostat |
| PHEV | Customer | Electric Vehicle |
| Phone/Email/Text/Web | Customer | Customer Equipment |
| Smart Appliance | Customer | Appliances |
| Smart Meter | Customer | Meter |
| Sub-Meter | Customer | Customer Equipment |
| Meter 2Way – Electric | Customer | Meter |
| Meter 2Way - Gas | Customer | Meter |
| Meter 2Way – Water | Customer | Meter |
| DAP | Customer / Distribution |  |
| Field Tool | Customer / Distribution |  |
| Capacitor Bank | Distribution | Field Device |
| Circuit Breaker | Distribution | Field Device |
| Recloser | Distribution | Field Device |
| Distributed Customer Generation | Distribution | Distribution Generation |
| Distributed Customer Storage | Distribution | Storage System |
| Sectionalizer | Distribution | Field Device |
| Switch | Distribution | Field Device |
| Regulator | Distribution | Field Device |
| DAC | Distribution / Transmission | Substation Controller |
| Distributed Generation | Distribution / Transmission | Distributed Generation |
| Distributed Storage | Distribution / Transmission | Storage System |
| FAN Gateway | Distribution / Transmission |  |
| Field Sensor | Distribution / Transmission | Field Device |
| RTU | Distribution / Transmission | Data Collector |
| Substation Devices | Distribution / Transmission | Substation Device |
| Energy Market Clearinghouse | Markets | Energy Market Clearinghouse |
| Retailer/Wholesaler | Markets | Aggregator/Retail Energy Provider |
| RTO/ISO | Markets | RTO/ISO |
| Aggregator | Markets / Service Providers | Aggregator |
|  | Operations | Asset Mgmt |
|  | Operations | WAMS |
| AMI Head-End | Operations | Metering System |
| Analytic Database | Operations |  |
| Distribution SCADA FEP | Operations | Distribution SCADA |
| DMS | Operations | DMS |
| EMS [RTO/ISO Ops] | Operations | EMS [RTO/ISO Ops] |
| EMS [Transmission Ops] | Operations | EMS [Transmission Ops] |
| GIS | Operations |  |
| GL / Accounts Payable / Receivable | Operations |  |
| MDMS | Operations | MDMS |
| NMS | Operations |  |
| OMS | Operations |  |
| RTO SCADA | Operations | RTO SCADA |
| Transmission SCADA FEP | Operations | Transmission SCADA |
| Work Management System | Operations |  |
| Certificate Authority | Operations / Service Provider |  |
| DSM [Distribution Ops / REP] | Operations / Service Provider | Demand Response |
| LMS [Distribition Ops / REP] | Operations / Service Provider |  |
| Security Key Manager [Distribution Ops / REP] | Operations / Service Provider |  |
| Bill Payment Orgs/Banks | Service Provider | Other |
| CIS/Billing [REP] | Service Provider | Billing [Retail Energy Provider] |
| CIS/Billing [REP] | Service Provider | CIS [Retail Energy Provider] |
| CIS/Billing [Utility] | Service Provider | CIS [Utility] |
| CIS/Billing [Utility] | Service Provider | Billing [Utility] |
| Common Web Portal-Jurisdictional | Service Provider | Other |
| Home/Building Manager | Service Provider | Home/Building Manager |
| Internet/Extranet Gateway [REP] | Service Provider |  |
| ODW [REP] | Service Provider |  |
| Web Portal [REP] | Service Provider |  |
| Web Portal [Utility] | Service Provider |  |

Table 2 - Actors

#### Identification of pertinent application payloads

While creating requirements the SG-Network team also documented the payloads’ general characteristics as the analysis was performed.  For each payload the following data was identified: payload name and type; general description, primary attributes, mapping to NISTIR 7628 v1.0 Logical Interface Categories (LICs); and security  confidentiality, integrity, availability (CIA) risk values along with rationale for those CIA values from an operational and business perspective.  For more information see the Application Payloads section in the Appendix 5.5. The figure that follows is illustrates the contents of that appendix.

Figure 2 Application Payload

#### Defining Business Functional and non-Functional (Volumetric) Requirements

There are many smart grid user applications (use cases) collections of documentation.  Many have text describing the user applications (see IKB), but few contain quantitative business functional and volumetric requirements, which are necessary to design communications protocols, to assess, or to plan communication networks.  Documenting the detailed actor to actor payloads and volumetric requirements allows for:

- aggregation of the details to various levels (e.g., specific interface or network link, a specific network or actor and have the supporting details versus making assumptions about those details) and

- allows the consumer of the Requirements Table to scope and customize the smart grid deployment specific to their needs (e.g., which set of use cases, payloads, actors, communication path deployments).

OpenSG_SG Communications_SG Network TF took on the task to document the Smart Grid business functional and volumetric requirements for input into the NIST PAP 2 tasks and to help fill this requirements documentation void.  The current SG-Network business functional and volumetric requirements are located at

- http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables/

with a file name syntax of “SG Network System Requirements Specification vN.R.xls”, where N represents the version number and R represents the revision number.  This spreadsheet is referred to below as the Requirements Table.

Instructions for how to document the business functional and volumetric requirements was prepared for the requirement authors, but also can be used by the consumer of the Requirements Table to better understand what is and is not included, and how to interpret the requirement data.  The requirements documentation instructions are located at:

- http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables/

with a file name syntax of “rqmts-documentation-instructions-rN.R.doc”, where N represents the version number and R represents the revision number.

The Requirements Table consists of several major sets of information for each use case:  For example:

- Business functional requirement statements are documented as individual information flows (e.g., specific application payload requirement sets). This is comparable to what many use case tools capture as information flows and/or illustrated in sequence diagram flows.

- To the baseline business requirements are added the:

volumetric attributes (the when, how often, with what availability, latency, application payload size).  Take note that the SG Network TF Requirements Table definition for some terms (e.g. latency) is different than the classic “network link latency” usage.  Please refer to the SG Network TF Requirements Documentation Instructions or section Requirements Table Column Descriptions

  - for the detailed definitions for clarification.

  - further payload details e.g. description, attributes, NISTIR 7628 security Logical Interface Category mapping, an assignment of the security confidentiality, integrity, and availability low-medium-high risk values, and business impacts of the payload being compromised as assessed against the security confidentiality, integrity, availability values for that application payload.

- Payload requirement sets are grouped by rows in the table that contains all the detailed actor to actor passing of the same application payloads in a sequence that follows the main data flow from that payload’s originating actor to primary consuming actor(s) across possible multiple communication paths that a deployment might use.  The payload requirements’ sets will always contain a parent (main) actor to actor row and most will contain child (detailed) rows for that requirement set.

- Payload communication path (information or data flow) alternatives that a given smart grid deployment might use.

The process of requirements gathering and documentation has been evolutionary in nature as various combinations of additional attributes are documented; use cases added; payload requirement sets added; and alternative communication paths documented. The SG Network TF has defined ~7875 (as of release 5.0) functional and volumetric detailed requirements rows in the Requirements Table representing 204 different payloads for 19 use cases.

SG Network TF intends to continue this incremental version release approach to manage the scope and focus on documenting the requirements for specific use cases and payloads, yet giving consumers of this information something to work with and provide feedback for consideration in the next incremental releases. We expect that the number of requirements rows in the Requirements Table will increase over time.

For background information, the following link is provided for more information on how requirements are derived:

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables/rqmts-documentation-instructions-r1.3.pdf

To effectively use the business functional and volumetric requirements, the consumer of the Requirements Table must:

- select which use cases and payloads are to be included

- select which communication path scenario (alternative) is to be used for each of the main information/data flows from originating actor to target consuming actor

- specify the size (quantity and type of devices) of the smart grid deployment

- perform other tweaks to the payload volumetrics to match that smart grid deployment’s needs e.g. specifying variables not specifically quantified or ranges are provided

The current Requirements Table as a spreadsheet is not very conducive to performing these tasks.  SG-Network TF is building a database that is synchronized with the latest release of the Requirements Table (spread sheet).  SG Network TF will be adding capabilities to the database to:

- solicit answers to the questions summarized above;

- query the database; and

- format and aggregate the query results for either reporting or exporting for use by other tools.

The current SG-Network TF Requirements Database and related use documentation are located at

- http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables/ Rqmts_Database/

Requirements Table Column Descriptions

The Requirements Table spreadsheet contains several worksheets, two of which contain the bulk of the documented requirements: “Reqmts-Combined”; “Payload_attrib_LIC-CIA-rtnl”. The columns of data for each of these two worksheets are described as follows.

Reqmts-Combined Worsksheet (tab)

- Rqmt Ref – is a reference to the original worksheet line number the requirement originally defined

- Row Type – indicates whether the requirement row is the parent row for the specific payload or a child requirement row of that specific payload requirement set

- Data-Flow Ref – is a reference to the architectural reference models lines (data flows or interfaces) between actors shown illustratively in this document and attached to this work as a separate file

- Data Flow From Actor – indicates the actor that is considered the sender of information noted in the Requirements Column

- Data Flow to Actor – indicates the actor that is considered the desired recipient of the information noted in the Requirements Column

- Requirements – is the actual application requirement.  Words like “shall” in this column are to be considered required, while words like “may” should be considered optional

- Payload Name – explains the scenario type of the requirement derived from the use case. (e.g. Bulk, On Demand for meter reading)

- Payload Type – indicates the category of the application payload

- Daily Clock Periods of Primary Occurrence – one or multiple periods of the day that the majority of the specific payload occurs

- How Often - describes the quantity and frequency of the specific application payload as it moves between the stated actors across the interface (data flow) that this requirement row addresses

- Reliability - the probability that an operation will complete without failure over a specific period or amount of time.

- Latency - Summation of actor (including network nodes) processing time and network transport time measured from an actor sending or forwarding a payload to an actor, and that actor processing (or consuming) the payload.

- App Payload Size – is an estimation of how many bytes are needed for the requirement as actual application payload exclusive of any added security, or network, or protocol overheads.

Payload_attrib_LIC_CIA_rtnl Worsheet (tab)

- Payload Name – this syncs with the Payload Name in the Reqmts-Combined worksheet

- Payload Type – this syncs with the Payload Type in the Reqmts-Combined worksheet

- Payload Description - explanation of what is the application payload use and intent

- Payload Attributes - the data elements that are included in the application payload. This excludes any additional security and/or telecommunication protocol(s) added data elements around the application payload.

- Security LICs - NISTIR 7628 – Logical Interface Category (LIC) derived and mapped (as closely as possible to typically no more than 2-3 LICs) from the NISTIR 7628 document volume 1, section 2.3 “Table 2.2 Logical Interfaces by Category” and remaining sections 2.3.x to the application payload

- Payload C-I-A Risk Values– Confidentiality, Integrity, Availability security risk levels as described in NISTIR 7628 document volume 1, section 3.2 “Table 3-1 Impact Levels Definitions” and assigned based on the application payload’s description, attributes, C-I-A rationale excluding other security or telecomm network protocol(s) overhead data elements

- Security C-I-A Risk Values Rationale– documents the business impacts of the payload being compromised as assessed against the security confidentiality, integrity, availability areas

## Terms and Definitions

The use of a common vocabulary has been of critical important in the development of this and other Smart Grid related work products.  All pertinent terms and definitions utilized in this document are listed in the appendix section of this document.

# Illustrative Reference Architecture Overview

In these section a few illustrative diagrams are included to help the reader of this document to understand the content.  These files are also available for reference at the following locations:

The reference model diagrams locations are in the SG-Network TF webpage folder:

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables/Diagrams

The SG-Network functional requirements table location is:

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Latest_Release_Deliverables

Figure 3 - Baseline Diagram Without Cross Domain & Network

Figure 4 - Baseline Diagram with Cross Domain & Network flows

Table 4 - Smart Grid Functional & Volumetric Business Requirements

### Alternative Paths

The reference architecture developed by the SG-Network task force was intentionally created to model multiple variations of implementations.  Due to the variations in utility service territory, architectural principles and topologies, multiple paths of communication will be used.   The diagram in figure 10 is an example of multiple paths communications will take.  See the Appendix section Alternatives Paths for more information.

Figure 5 – Utility CIS <-> Meter Communication Path Scenarios

# Use Cases and Communications Requirements

## Overview and Context

The use cases listed in this section are intended to provide a summarization of the various use cases reviewed and analyzed by the SG Network WG.  The corresponding use case requirements listed in this document represent the most conservative requirements gathered from the utilities that participated in the SG Network WG and illustrated as reference for the worst case scenario.  In actual practice readers should establish requirements that best address the objectives of their company’s specific business case and operational requirements.

For purposes of organization, the use cases are represented in the context of the eight priority areas outlined by NIST in the “NIST Framework and Roadmap for Smart Grid Interoperability Standards, Release 1.0”.  The authors have chosen to organize the use case summaries in a manner as to provide traceability between the NIST priority areas and the contents of this document.

Wherever possible the use cases have been summarized in order to provide a concise account of the process, actors and requirements.  Additional information relating to the use cases is available at the SG Network Share point.

## Customer Information & Messaging

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| --- | --- |
| Cust. Browser - Mobile | A mobile device World Wide Web compliant internet browser (e.g. Internet Explorer, Google Chrome, Safari, Mozila Firefox) used by a customer. |
| Cust. Browser - Premise | A World Wide Web compliant internet browser (e.g. Internet Explorer, Google Chrome, Safari, Mozila Firefox) used within a customers premises. |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| ODW - REPi | Operational Data Warehouse |
| ODW - Utility | Operational Data Warehouse |
| Web Portal – REPi | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |
| Web Portal – Utility | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Dispatched Distributed Customer Storage

[Ed note: this document includes 2 sets of usecases: Load Management (a.k.a. ‘Direct Load Control’) and Demand Response]

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| DAC - Ops/Regnl | Distribution Application Control system hosted in either the Utilities Operations or Regional Data Centers to run a specific Distrbution application |
| --- | --- |
| DAC – sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| Distr. Cust. Storage | Distributed Customer Storage is a storage device sized to meet typical distribution substation circuit loads and is typically located at or near a distribution substation or in smaller capacities out in customer/premise neighborhoods |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Circuit Breaker | A device used in the substation that is used per a specific configuration to protect distribution equipment. |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Direct Load Management

### Overview

The Load Management (a.k.a. ‘Direct Load Control’) use cases described in this body of work include the following scenarios.  For each scenario the primary command, response and failure payloads are described

- Load Management Request

- Voluntary Load Shed Request

- Load Management Request Opt-Out

- (what about Cancel Load Management?)

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| DSM - REPi | Demand Side Management - Retail Energy Provider; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| DSM - Utility | Demand Side Management - Utility; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| EVSE / EUMD | Electric Vehicle Supply Equipment / End Use Metering Device |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| LMS - REPi | Load management system |
| LMS - Utility | Load management system - System that controls load by sending messages directly to device (e.g. On/Off) |
| Load Cntl Device | A device used within the customer domain for load management (e.g. Air conditioning, etc) |
| PCT | A device within the premise that has communication capabilities and controls heating, ventilation and cooling systems. |
| PHEV | Plug-in Hybrid Electric Vehicles - Cars or other vehicles that draw electricity from batteries to power an electric motor for vehicle propulsion. PHEVs also contain an internal combustion engine. |
| Smart Appliance | A white good or household appliance, that has HAN communication capability and is capable of receiving signals from authorized parties (e.g. Utility, Service Provider, EMS, Consumer, etc.) and of adjusting its operational mode based on Consumer preference |

### Scenarios

#### Scenario: Load Management Request

Narrative

The Load Management Request is used to mandatory communicate energy management requests to the end use consumer devices to manage load on the distribution network.

In this scenario, the request originates at the Load Management System or Demand Side Management system where it is transferred to the AMI headend for transmission to the ESI.

Transmission from the AMI head-end to the ESI can occur in several ways:

- Via the WAN, through the DAP, via the AMI network

- through the Internet/Extranet gateway(s), via the Internet/Extranets and WAN, through the DAP via the AMI network

- through the Internet/Extranet gateway(s), via the Internet/Extranets and Customer LAN

From the ESI, the message is forwarded to the appropriate HAN device (Appliance, PHEV, Load control Device).  The HAN device will acknowledge the receipt of the information and initiate the appropriate action.

The acknowledgement typically follows the revers path to the LMS or DSM, i.e.  via the AMI network through the DAP to the AMI Headend, or alternatively, via the Internet/Extranets through the Internet/Extranet gateway DAP to the AMI Headend, from where the message is then forwarded to LMS or DSM.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| LMS or DSM | ESI | < 20 seconds | 98% | 100 bytes | Load_mgm_reqst |
| LMS or DSM | ESI | < 20 seconds | 99.5% | 100 bytes | Load_mgm_reqst_brdcst |
| LMS or DSM | ESI | < 20 seconds | 98% | 100 bytes | Load_mgm_reqst_mltcst |
| ESI | LMS or DSM | < 20 seconds | 98% | 25 bytes | Load_mgm_req_ack |
| Totals | < 40seconds | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot receive Load Management event |
| Distribution | X | Cannot reduce load. |
| Markets |  |  |
| Operation | X | Systems will have to retry communications or cannot achieve savings |
| Service Providers | X | Reps will not be able to perform load management |
| Transmission |  |  |

#### Scenario: Voluntary Load Shed Event Notification

Narrative

Voluntary Load Shed Requests are  used to communicate voluntary energy management requests to the end use consumer devices to manage load on the distribution network.

In this scenario, the request originates at the Load Management System or Demand Side Management system where it is transferred to the AMI head-end for transmission to the ESI.

Transmission from the AMI head-end to the ESI can occur in several ways:

- Via the WAN, through the DAP, via the AMI network

- through the Internet/Extranet gateway(s), via the Internet/Extranets and WAN, through the DAP via the AMI network

- through the Internet/Extranet gateway(s), via the Internet/Extranets and Customer LAN

From the ESI, the message is forwarded to the appropriate HAN device (Appliance, PHEV, Load control Device).  The HAN device will acknowledge the receipt of the information and initiate the appropriate action.

The acknowledgement typically follows the revers path to the LMS or DSM, i.e.  via the AMI network through the DAP to the AMI Headend, or alternatively, via the Internet/Extranets through the Internet/Extranet gateway DAP to the AMI Headend, from where the message is then forwarded to LMS or DSM.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| LMS or DSM | ESI | < 20 seconds | 98% | 100 bytes | Vol_load_shed_reqst |
| LMS or DSM | ESI | < 20 seconds | 99.5% | 100 bytes | Vol_load_shed_reqst_brdcst |
| LMS or DSM | ESI | < 20 seconds | 98% | 100 bytes | Vol_load_shed_reqst_mltcst |
| ESI | LMS or DSM | < 20 seconds | 98% | 25 bytes | Vol_load_shed_req_ack |
| Totals | < 40seconds | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot receive Voluntary Load Shed event |
| Distribution | X |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications or cannot achieve savings |
| Service Providers | X |  |
| Transmission |  |  |

#### Scenario: Load Management Request Opt-Out

Narrative

Load Management Opt-Out  is used to communicate a consumer’s decision to opt-out of a Voluntary Load Management Request.

In this scenario, the end-device that receives a Voluntary Load Management Request decides to opt-out, and a message is sent up to the LMS or DSM.

Transmission to the LMS or DSM can occur via the AMI network through the DAP to the AMI Headend, or alternatively, via the Internet/Extranets through the Internet/Extranet gateway DAP to the AMI Headend

Transmission from the ESI to the LMS or  DSM can occur via several paths:

- Via the AMI network through the DAP via the WAN

- Via the AMI network through the DAP via the WAN and/or Internet through   Internet/Extranet gateway(s)

- Via Customer LAN and Internet/Extranets, through the Internet/Extranet gateway(s)

From the AMI head-end the message is then forwarded to LMS or DSM.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Consumer Device | LMS or DSM | < 20 seconds | 98% | 25 bytes | Load_mgm_opt_out |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot opt-out. |
| Distribution | X | Potential impact if too many opt out requests are made |
| Markets |  |  |
| Operation | X | Systems will not be able to adjust management strategy |
| Service Providers | X | Potential impact if too many opt out requests are made |
| Transmission |  |  |

## Demand Response and Consumer Energy Efficiency

### Overview

The Demand Response and Consumer Energy Efficiency use cases described in this body of work include the following scenarios.  For each scenario the primary command, response and failure payloads are described

- Price Event Notification

- Consumer Message Notification

- (Ack, etc?)

#### Reference Architecture with Domains, Actors, and Interfaces

#### Possible Communications Paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| DSM - REPi | Demand Side Management - Retail Energy Provider; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| DSM - Utility | Demand Side Management - Utility; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| EVSE / EUMD | Electric Vehicle Supply Equipment / End Use Metering Device |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| LMS - REPi | Load management system |
| LMS - Utility | Load management system - System that controls load by sending messages directly to device (e.g. On/Off) |
| Load Cntl Device | A device used within the customer domain for load management (e.g. Air conditioning, etc) |
| PCT | A device within the premise that has communication capabilities and controls heating, ventilation and cooling systems. |
| PHEV | Plug-in Hybrid Electric Vehicles - Cars or other vehicles that draw electricity from batteries to power an electric motor for vehicle propulsion. PHEVs also contain an internal combustion engine. |
| Smart Appliance | A white good or household appliance, that has HAN communication capability and is capable of receiving signals from authorized parties (e.g. Utility, Service Provider, EMS, Consumer, etc.) and of adjusting its operational mode based on Consumer preference |

### Scenarios

#### Scenario: Price Event Notifications

Narrative

The Price Event Notification is used to communicate energy management requests to the end use consumer devices to manage load on the distribution network.

In this scenario, the event originates at the Load Management System or Demand Side Management system where it is transferred to the AMI head-end for transmission to the ESI.

Transmission to the ESI can occur through the DAP via the AMI network, or alternatively, through the Internet/Extranet gateway via the Internet/Extranets.

From the ESI, the message is forwarded to the appropriate HAN device (IHD, PCT, Appliance, PHEV, etc).  The HAN device will acknowledge the receipt of the information and initiate the appropriate action, e.g., adjust its load based on the current price tier.

The acknowledgement typically follows the revers path to the LMS or DSM, i.e.  via the AMI network through the DAP to the AMI Headend, or alternatively, via the Internet/Extranets through the Internet/Extranet gateway DAP to the AMI Headend, from where the message is then forwarded to LMS or DSM.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| LMS or DSM | ESI | ? | 98% | 100 bytes | (price signal event) |
| ESI | LMS or DSM | ? | 98% | 25 bytes | (ack?) |
| Totals |  | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access the price of energy and adjust behavior |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers |  |  |
| Transmission |  |  |

#### Scenario: Consumer Message Notifications

Narrative

The Consumer Message Notification is used to communicate energy  related information to the end use consumer devices on the distribution network that are capable of displaying this.  In this scenario, the event originates at the Demand Side Management System where it is transferred to the AMI head-end for transmission to the meter/ESI.  From there, the message is forwarded to the appropriate HAN device (IHD, PCT, Appliance, PHEV).

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| LMS or DSM | ESI |  | 98% | 100 bytes | (message event) |
| ESI | LMS or DSM |  | 98% | 25 bytes | (ack?) |
| Totals |  | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access energy related announcements and adjust behavior |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | ? |
| Service Providers |  |  |
| Transmission |  |  |

## Distribution System Demand Response – Centralized Control

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| --- | --- |
| DAC - sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - field | Field Area Network gateway device located in the field, that provides the interface between the Feeder Line device communication modules and the Wide Area Network connection. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Cap Bank | This is a device used to add capacitance as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Feeder Regulator | This device is in effect an adjustable ratio transformer positioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| Feeder Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Distribution System Demand Response – De-Centralized Control

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Fault Clear Isolate – Distribution DAC

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| DAC - sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| --- | --- |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Circuit Breaker | A device used in the substation that is used per a specific configuration to protect distribution equipment. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| OMS | A system that receives power system outage notifications and correlates the geographic location of the power outage |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Fault Clear Isolate – Distribution Management System

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| --- | --- |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Circuit Breaker | A device used in the substation that is used per a specific configuration to protect distribution equipment. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| OMS | A system that receives power system outage notifications and correlates the geographic location of the power outage |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Fault Clear Isolate – Regional Distribution DAC

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| DAC - Ops/Regnl | Distribution Application Control system hosted in either the Utilities Operations or Regional Data Centers to run a specific Distrbution application |
| --- | --- |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Circuit Breaker | A device used in the substation that is used per a specific configuration to protect distribution equipment. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| OMS | A system that receives power system outage notifications and correlates the geographic location of the power outage |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Field Distribution Automation Maintenance – Centralized Control

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| --- | --- |
| DAC - sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - field | Field Area Network gateway device located in the field, that provides the interface between the Feeder Line device communication modules and the Wide Area Network connection. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Cap Bank | This is a device used to add capacitance as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Regulator | This device is in effect an adjustable ratio transformer positioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| Feeder Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Firmware / Program Update

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| 2-Way Meter - Gas | A bi-directional communication device used to perform measurement of gas consumption for residential use. |
| 2-Way Meter - Water | A bi-directional communication device used to perform measurement of water consumption for residential use. |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Distr. Cust. Generation | Distributed Customer Generation is a generation source sized to meet typical distribution substation circuit loads and is typically located at or near a distribution substation |
| Distr. Cust. Storage | Distributed Customer Storage is a storage device sized to meet typical distribution substation circuit loads and is typically located at or near a distribution substation or in smaller capacities out in customer/premise neighborhoods |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - In Meter, ESI - Utility | A combination of ESI - In Meter and ESI - Utility for determining the exact quantity of payloads to be associated to a DAPjm |
| ESI - In Meter, ESI - Utility, ESI - 3rd Party | A combination of ESI - In Meter and ESI - Utility and ESI - 3rd Party for determining the exact quantity of payloads to be associated to a DAPjm |
| ESI – Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| FAN gateway – field | Field Area Network gateway device located in the field, that provides the interface between the Feeder Line device communication modules and the Wide Area Network connection. |
| FAN gateway - field, FAN gateway - sub | A combination of FAN gateway - field and FAN gateway - sub for determining the exact quantify of payloads to the Feeder Line devices |
| FAN gateway – sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Cap Bank | This is a device used to add capacitance as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Regulator | This device is in effect an adjustable ratio transformer positioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| Feeder Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| Field Tool | A device used in the distribution operations and customer domain to perform configuration and maintenance of devices. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Islanded Distribution Customer Storage

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter – Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAC - Ops/Regnl | Distribution Application Control system hosted in either the Utilities Operations or Regional Data Centers to run a specific Distrbution application |
| DAC – sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI – Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| FAN gateway – field | Field Area Network gateway device located in the field, that provides the interface between the Feeder Line device communication modules and the Wide Area Network connection. |
| FAN gateway – sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| LMS – Utility | Load management system - System that controls load by sending messages directly to device (e.g. On/Off) |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| OMS | A system that receives power system outage notifications and correlates the geographic location of the power outage |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Electric Transportation

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Meter Reading Use Cases

### Overview

The Meter Reading use cases described in this body of work include the following scenarios.  For each scenario the primary command, response and failure payloads are described

- On Demand Meter read

- On Demand Meter read failure

- On Demand Meter interval period read

- Bulk Meter Interval data read

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communications paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| 2-Way Meter - Gas | A bi-directional communication device used to perform measurement of gas consumption for residential use. |
| 2-Way Meter - Water | A bi-directional communication device used to perform measurement of water consumption for residential use. |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| CIS/Billing - Utility | A utility billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| NMS | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |

### Scenarios

#### Scenario: On-Demand Meter Reading

Narrative

Electric meters are anticipated to have on-demand meter reading capability.  In this scenario, the request may originate from the CIS or the MDMS.  In any case, we expect the head end to receive on demand meter read request and forward the request to the Smart Meter via the DAP.  Smart meters may be read on demand for purposes of backfilling missing information, customer interaction or move in and move out scenarios.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| MDMS | Smart Meter | < 15 seconds | 98% | 25 bytes | on-demand_Mtr-read_cmd |
| Smart Meter | MDMS | < 15 seconds | 98% | 200-400 bytes | On-demand_Mtr-read_rspns_data |
| Totals | < 30 seconds | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access recent usage information. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers | X | Cannot acquire specific recent meter usage information. |
| Transmission |  |  |

#### Scenario On-Demand Read Failure

Narrative

Electric meters are anticipated to have on-demand meter reading failure.  In this scenario, the request may originate from the CIS or the MDMS.  In any case, we expect the Smart Meter on demand read request to fail and at each step of the process, if a failure occurs, the upstream devices shall send a notification of failure.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| MDMS | Smart Meter | < 15 seconds | 98% | 25 bytes | on-demand_Mtr-read_cmd_comm_err |
| Smart Meter | MDMS | < 15 seconds | 98% | 25 bytes | on-demand_Mtr-read_cmd_err |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access recent usage information. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers | X | Cannot acquire specific recent meter usage information. |
| Transmission |  |  |

#### Scenario: Bulk Meter interval read

Narrative

Electric and Gas utilities wish to obtain electric and gas consumption data four to six times a day.  During these four to six operations per day, the operation shall obtain interval usage information varying from 15 minutes to 1 hour in duration since the last successful bulk read operation.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | < 3 hour | 98% | 200-1600 bytes | Mtr-read_multi-interval-data_resp-data |
| Totals | < 3 hour | 98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access recent usage information. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers | X | Cannot acquire specific recent meter usage information. |
| Transmission |  |  |

## Outage and Restoration Management

### Overview of Business Processes

The following sections outline business use cases for Outage and Restoral Management.  This management pertains to many forms of information that is exchanged between the communication actors.

The implementations of these use cases, and their accompanying requirements, will vary from utility to utility.  Some examples of factors that will cause variations are:

Environmental (Earthquake/creep, Weather, Seasonal, Topography, etc)

Demographic (Residential, Industrial, etc)

The author’s intent is to capture the numerous use case requirements across the communication actors in the scope of the management of this information.  The intent is to reflect which use cases can be applied to different aspects of the Utility/Customer.

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| --- | --- |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| NMS | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |
| OMS | A system that receives power system outage notifications and correlates the geographic location of the power outage |

### Scenarios – Off AC Power

All communication actors run of some form of power system.  The failure of the AC power source can affect many aspects of the service and business.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | DAP | < 20 seconds | > 30% large outage, > xx% small outage | 25 bytes | otg_ntf_evnt_data |
| Totals | < 20 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot access recent usage information. |
| Distribution | X | Potential Infrastructure is offline. |
| Markets |  |  |
| Operation | X | Utility may need to roll personnel. |
| Service Providers | X | Cannot acquire specific recent meter usage information. |
| Transmission |  |  |

### Scenarios – Battery Backup State

When main power source is lost and the actor is running off a backup power source, an important alarm is the state of the backup system.  The assumption is the meter is still functional.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | DAP | < 5 seconds | > 99% | 25 bytes | btry_pwr_notification |
| Totals | < 5 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Utility may need to roll personnel |
| Service Providers |  |  |
| Transmission |  |  |

### Scenarios – Electric Power Restoration

When the power source of the actor is restored, there is an alert to notify the destination that the originating actor is back online.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | DAP | < 20 seconds | > 98% | 25 bytes | svc_rst_ntf_evnt_data |
| Totals | < 20 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Can now read recent usage information. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Utility may be able to stop roll of personnel |
| Service Providers | X | Can now acquire specific recent meter usage information. |

### Scenarios – Off AC Power

All communication actors run of some form of power system.  The failure of the AC power source can affect many aspects of the service and business.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DAP | AMI Head End | < 20 seconds | > 99% | 25 bytes | otg_ntf_evnt_data |
| AMI Head End | DAP | < 20 seconds | > 99% | 25 bytes | otg_ntf_evnt_data |
| Totals | < 40 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution | X | May not be able to communicate with endpoint |
| Markets |  |  |
| Operation | X | Utility may need to roll personnel. |
| Service Providers |  |  |
| Transmission |  |  |

### Scenarios – Battery Backup State

When main power source is lost and the actor is running off a backup power source, an important alarm is the state of the backup system.  The assumption is the meter is still functional.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DAP | AMI Head End | < 20 seconds | > 99% | 25 bytes | btry_pwr_notification |
| AMI Head End | DAP | < 20 seconds | > 99% | ??? | No ACK defined???????? |
| Totals | < 40 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Utility may need to roll personnel |
| Service Providers |  |  |
| Transmission |  |  |

### Scenarios – Electric Power Restoration

When the power source of the actor is restored, there is an alert to notify the destination that the originating actor is back online.

Business Objectives

Need to add an acknowledgement optional payload

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DAP | AMI Head End | < 20 seconds | > 98% | ?? | No Alarm defined???????? |
| AMI Head End | DAP | < 20 seconds | > 98% | ??? | No ACK defined???????? |
| Totals | < 40 seconds |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Utility may be able to stop roll of personnel |
| Service Providers |  |  |

## System Events

### Overview

The following section identifies network requirements for enabling and processing system events and use cases associated with the Smart Grid.  This document does not address, establish or recommend any security requirements or supporting architectures needed for the Smart Grid.  Smart Grid security is being addressed in detail by other functioning task forces within the OpenSG and the UCAIUG.  The intent is to establish a straw man set of requirements to be incorporated into the overall Smart Grid network design for addressing security communication requirements.

Below is an example architecture showing the Domains, Actors, and Interfaces used in this use case.

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible Communications Paths

### Actors

| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| --- | --- |
| CIS/Billing - Utility | A utility billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |

### Scenarios

#### Scenario:Security Event

Narrative

The objective is to collect alarms from the meter that occur when a meter is driven to an out of state condition.  The communication of the event information is triggered locally on the meter in response to pre defined condition.  The metric to judge the state or condition are locally store on the meter device.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | <2 min | >98% | 25-278 bytes | Security_Event |
| Totals | <2 min | >98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer's service could be affected. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Smart Meter could require maintenance. |
| Service Providers |  |  |
| Transmission |  |  |

#### Scenario: Audit Event

Narrative

The objective is to collect events from the meter that occur when there is a failure or exception in the execution of a request or an internal application function.  Audit events are considered to be time based or on demand.  The time based events could be driven by the validation the registers within the meter are still valid.  Application events can be caused by a running application not performing as designed and reporting an error or a running application on the meter causing a threshold to be reached and triggering an event.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | <4 min | >98% | 25-278 bytes | Audit_Application_Event |
| Totals | <4 min | >98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer's service could be affected. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Smart Meter could require maintenance. |
| Service Providers |  |  |
| Transmission |  |  |

#### Scenario: Configuration Event

Narrative

The objective is to collect events from the meter that occur when there is a out of state condition with the configuration on the meter.  The configuration events are focused on maintaining metrics that define the meters operating state.  Unlike other events that have a high and low limit thresholds the configuration events are thought to not any thresholds.  The event would be trigged on the meter by a state outside of a defined metric for configuration.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | <2 min | >98% | 25-278 bytes | Configuration_Event |
| Totals | <2 min | >98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer's service could be affected. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Smart Meter could require maintenance. |
| Service Providers |  |  |
| Transmission |  |  |

#### Scenario: Fault Error Alarm Event

Narrative

The objective is to collect alarms from the meter that occur when there is an out of state or passed a threshold condition on the meter.  The communication of the event information is triggered locally on the meter in response to reaching a pre defined condition.  The metric to judge the state or condition are locally store on the meter device.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | <2 min | >98% | 25-278 bytes | Fault_Error_Alarm_Event |
| Totals | <2 min | >98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer's service could be affected. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Smart Meter could require maintenance. |
| Service Providers |  |  |
| Transmission |  |  |

#### Scenario: Power Quality Event

Narrative

The objective is to collect alarms from the meter that occur when there is a out of state or passed a threshold condition on the meter.  Power quality event are disturbance oriented by nature, leading / lagging power.  In most cases the events will be as result of excessive steady state voltage variation, unbalance in energy flow, harmonics on the line, sags, swells, oscillatory.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Smart Meter | MDMS | <2 min | >98% | 25-278 bytes | Power_Quality_Event |
| Totals | <2 min | >98% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer's service could be affected. |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Smart Meter could require maintenance. |
| Service Providers |  |  |
| Transmission |  |  |

## System Security

### Overview

The following section identifies network requirements for enabling and processing security events and use cases associated with the Smart Grid.  This document does not address, establish or recommend any security requirements or supporting architectures needed for the Smart Grid.  Smart Grid security is being addressed in detail by other functioning task forces with in the OpenSG and the UCAIUG.  The intent is to establish a straw man set of requirements to be incorporated into the overall Smart Grid network design for addressing security communication requirements.

#### CIA

The team has identified the CIA values for the specific network transactions associated with the network security events and use cases.  The CIA designations are based on the types of transactions and payloads being transmitted by the respective actors.  The CIA designations are included in the accompanying databases and spreadsheets that compromise the SRS.

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Customer Information System | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |  |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| Enterprise Service Bus | This is an integration bus utilized for integrating disparate applications. The ESB is also used as a translation engine that can translate and harmonize messages and transactions between systems. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Network Management System | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |  |
| Internet / Extranet Gateways | These are gateways used to connect internal utility networks with external networks. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Repeater | A repeater is used in radio frequency networks as a means of extending the each of the network. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |
| Smart Meter – Energy Services Interface | This is the interface utilized to communicate directly between the Smart Meter and the Customer HAN or EMS system. This interface is used to allow utilities and third parties to communicate with the customer via the AMI system. |  |

Table 9 - Metering Audit Event Actors

### Audit Event

#### Objective

The objective is to collect events from the meter that occur when there is a failure or exception in the execution of a request or an internal application function.  Audit events are considered to be time based or on demand.  The time based events could be driven by the validation the registers within the meter are still valid.  Application events can be caused by a running application not performing as designed and reporting an error or a running application on the meter causing a threshold to be reached and triggering an event.

#### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |

Table 10 - Metering Security Event Actors

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| Smart Meter | DAP | Event Driven | <1 min | Medium |
| DAP | AMI Head End | Event Driven | <1 min | Medium |
| AMI Head End | MDMS | Event Driven | <1 min | Medium |

Table 11 - Latency Requirements

#### Process Flow

Figure 6 - Process Flow

#### Included Processes

## Network Communications –

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Configuration Event (Ron)

#### Objective

The objective is to collect events from the meter that occur when there is a out of state condition with the configuration on the meter.  The configuration events are focused on maintaining metrics that define the meters operating state.  Unlike other events that have a high and low limit thresholds the configuration events are thought to not any thresholds.  The event would be trigged on the meter by a state outside of a defined metric for configuration.

#### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |

Table 12 - Metering Configuration Event Actors

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| Smart Meter | DAP | Event Driven | <30 sec | High |
| DAP | AMI Head End | Event Driven | <30 sec | High |
| AMI Head End | MDMS | Event Driven | <30 sec | High |

Table 13 - Latency Requirements

#### Process Flow

Figure 7 - Process Flow

#### Included Processes

### Fault Error Alarm Event

#### Objective

The objective is to collect alarms from the meter that occur when there is an out of state or passed a threshold condition on the meter.  The communication of the event information is triggered locally on the meter in response to reaching a pre defined condition.  The metric to judge the state or condition are locally store on the meter device.

#### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |

Table 14 - Metering Fault Alarm Actors

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| MDMS | Smart Meter | Event Driven | <15 sec | Medium |
| Smart Meter | MDMS | Event Driven | <15 sec | Medium |

Table 15 - Latency Requirements

#### Process Flow

Figure 8 - Process Flow

#### Included Processes

## Performance Management

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Premises Network Administration

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| 2-Way Meter - Gas | A bi-directional communication device used to perform measurement of gas consumption for residential use. |
| 2-Way Meter - Water | A bi-directional communication device used to perform measurement of water consumption for residential use. |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| CIS/Billing - REPi | A third party billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| CIS/Billing - Utility | A utility billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| EVSE / EUMD | Electric Vehicle Supply Equipment / End Use Metering Device |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| Load Cntl Device | A device used within the customer domain for load management (e.g. Air conditioning, etc) |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| NMS | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |
| PCT | A device within the premise that has communication capabilities and controls heating, ventilation and cooling systems. |
| PHEV | Plug-in Hybrid Electric Vehicles - Cars or other vehicles that draw electricity from batteries to power an electric motor for vehicle propulsion. PHEVs also contain an internal combustion engine. |
| Smart Appliance | A white good or household appliance, that has HAN communication capability and is capable of receiving signals from authorized parties (e.g. Utility, Service Provider, EMS, Consumer, etc.) and of adjusting its operational mode based on Consumer preference |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Electric Service Prepayment

### Overview

The Electric Service Prepayment use cases described in this body of work include the following scenarios.  For each scenario the primary command, response and failure payloads are described

- Customer Enroll or Un Enroll and Meter Configuration

- On-Demand Meter Read

- On-Demand Meter Read Errors

- PrePay Messaging to Customer

- Customer Payments

- Service Switch Operation

- Service Switch Operation Errors

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communications paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| 2-Way Meter - Gas | A bi-directional communication device used to perform measurement of gas consumption for residential use. |
| 2-Way Meter - Water | A bi-directional communication device used to perform measurement of water consumption for residential use. |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| CIS/Billing - REPi | A third party billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| CIS/Billing - Utility | A utility billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| NMS | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |
| Web Portal - REPi | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |
| Web Portal - Utility | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |

### Scenarios

#### Customer Enroll or Un-Enroll and Meter Configuration

Narrative

Electric meters may be enrolled in prepayment programs through the use of customer requests to the CIS infrastructure.  There are several sources of the enroll request that can be collapsed into two basic types, one from browsers at the customer premise and one from the customer mobile browser.  Specified here are two collapsed un-enroll use cases for premise and mobile browser requests.

Business Objectives

##### Customer Enroll Mobile Browser

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Cust. Browser - Mobile | CIS | < 30s | >99% | 100 | prepay_cust_enroll_cmd |
| CIS/Billing - Utility | Meter | < 1m | >98% | 25 | prepay_meter_config_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS | < 1m | >98% | 25 | SW_opr_cmd_ack |
| Totals | < 2:30m | >95% | 150 |  |

##### Customer Enroll Premise Browser

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Cust. Browser - Premis | CIS | < 15s | >99% | 100 | prepay_cust_enroll_cmd |
| CIS/Billing - Utility | Meter | < 1m | >98% | 25 | prepay_meter_config_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS | < 1m | >98% | 25 | SW_opr_cmd_ack |
| Totals | < 2:15m | >95% | 150 |  |

##### Customer Un-Enroll Mobile Browser

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Cust. Browser - Mobile | CIS | < 30s | >99% | 100 | prepay_cust_unenroll_cmd |
| CIS/Billing - Utility | Meter | < 1m | >98% | 25 | prepay_meter_config_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS | < 1m | >98% | 25 | SW_opr_cmd_ack |
| Totals | < 2:30m | >95% | 150 |  |

##### Customer Enroll Premise Browser

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Cust. Browser - Premis | CIS | < 15s | >99% | 100 | prepay_cust_unenroll_cmd |
| CIS/Billing - Utility | Meter | < 1m | >98% | 25 | prepay_meter_config_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS | < 1m | >98% | 25 | SW_opr_cmd_ack |
| Totals | < 2:15m | >95% | 150 |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot enroll or un-enroll prepay services |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers |  |  |
| Transmission |  |  |

#### On-Demand Meter Read

See Section X.X.X.X On-Demand Meter Read

#### On-Demand Meter Read Errors

See Section X.X.X.X On-Demand Meter Read Errors

#### PrePay Messaging to Customer

Narrative

The CIS actors may need to send messages to PrePay customers from time to time to inform customers on items like price, available credit, or general broadcast messages.  The CIS actor can send messages to different actors which are the IHD, the Customer EMS.  The communication characteristics can be collapsed for simplification to one use case shown below.

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| CIS | Cust. EMS Or IHD | < 30s | >99.5% | 50 -100 | prepay_msg_[1of10]_resp-data |
| Cust. EMS Or IHD | CIS | ? | ? | ? | ?????_resp_data_ack |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Cannot enroll or un-enroll prepay services |
| Distribution |  |  |
| Markets |  |  |
| Operation | X | Systems will have to retry communications |
| Service Providers |  |  |
| Transmission |  |  |

#### Customer Payments

Narrative

Customers must make payments in order to continue to receive electric service.  Non-payment will ultimately result in a meter disconnection of service.  It is assumed that the payment and credit activities are out of scope from this document.  Customer account levels and the display of that information on the IHD are in scope.

The use cases described above for PrePay Messaging to Customers is assumed to cover this use case.

#### Service Switch Operation

Narrative

Service Switch Operations are used within these use cases for the purpose of shutting off electric service to those PrePay customers who have not paid for service and have run out of funds in their accounts.  The process for determining account funding are out of scope for this document.  This use case will begin with the need of the CIS actors to operate the service swith on or off.

It is assumed that there are other use cases describing service switch operation.

Business Objectives

##### Service Switch Operation – Turn Off – Response from Meter state is OFF

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| CIS/Billing - Utility | Smart Meter | < 1m | > 98% | 25 | SW_state_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS, LMS, DSM | < 1m | > 98% | 100 | SW_state_cmd_resp-data |
| Totals |  |  |  |  |

##### Service Switch Operation – Turn Off – Response from Meter state is ON – no comm. errors

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| CIS/Billing - Utility | Smart Meter | < 1m | > 98% | 25 | SW_state_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS, LMS, DSM | < 1m | > 98% | 100 | SW_state_cmd_resp-data |
| CIS/Billing - Utility | Smart Meter | < 1m | > 98% | 25 | SW_opr_cmd |
| Smart Meter | CIS/Billing - Utility, MDMS | < 3m | > 98% | 25 | SW_opr_cmd_ack |
| Totals |  |  |  |  |

##### Service Switch Operation – Turn Off – Response from Meter state is ON – With comm. errors

| Sequence | Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | CIS/Billing - Utility | Smart Meter | < 1m | > 98% | 25 | SW_state_cmd |
| 2 | Smart Meter | CIS/Billing - Utility, MDMS, LMS, DSM | < 1m | > 98% | 100 | SW_state_cmd_resp-data |
| 3 | CIS/Billing - Utility | Smart Meter | < 1m | > 98% | 25 | SW_opr_cmd |
| 4 | Smart Meter | CIS/Billing - Utility, MDMS | < 3m | > 98% | 50 | SW_opr_fail_cmd-err |
| 4 | DAP | CIS/Billing - Utility, MDMS, NMS | < 1m | > 99% | 50 | SW_opr_cmd_comm-err |
| 4 | Smart Meter | CIS/Billing - Utility, MDMS | < 3m | > 98% | 50 | SW_opr_fail_cmd-err |
|  | Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

#### Service Switch Operation Errors

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Distribution Grid Management

### Overview of Business Processes

The following sections outline business use cases for distribution automation.  Distribution Automation represents a fairly complex set of use cases and requirements.  The implementations of these use cases, and their accompanying requirements, will vary from utility to utility.  In addition, the implementation of distribution automation assets is not uniform across utilities.

The association of devices to specific use cases will vary across different distribution monitoring and control devices.  The author’s intent is to capture the numerous use case requirements across these monitoring and control devices.  The intent is to reflect which use cases can be applied to different distribution automation devices.

Since utility’s Distribution Automation implementations vary, the authors wished to provide a menu of different devices and use cases that could be customized to specific utility needs.

Initially we define the use cases by their respective business process.  Since Distribution Automation is a complex application, encumbering numerous applications that can be implemented in a number of ways, we have attempted to map the Distribution Automation business processes to specific distribution devices in an effort to provide an accurate depiction of the roles and uses relating different devices in a distribution network.

### Business Process Definitions

#### Maintenance

##### Overview

Physical distribution devices require maintenance procedures to make sure that the equipment is functioning properly.  These procedures can include self checks on equipment, poling equipment at scheduled intervals, and reading sensor data to monitor equipment conditions.  There are several devices that fall into this category.  The term Feeder Line Device is used to represent any of the following in this maintenance use case:

- Capacitor Bank Controller (CBC)

- Fault Detector

- Recloser

- Line Sensor

- Switch

- Voltage Regulator

###### Scenario: Feeder Line Device Alarm

Narrative

The Feeder Line Device sends an alarm to SCADA that is operating improperly.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_alarm FeederFault_Detector_alarm FeederRecloser_alarm FeederSensor_alarm FeederSwitch_alarm FeederVR_alarm |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Feeder Line Device Deviation Alert

Narrative

The Feeder Line Device sends an alarm to SCADA that is operating outside of its normal boundaries.  An example of this would be the system voltage drops under a predetermined level.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_deviation_alert FeederFault_Detector_deviation_alert FeederRecloser_deviation_alert FeederSensor_deviation_alert FeederSwitch_deviation_alert FeederVR_deviation_alert |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | CBC groupings not functional for mass operation. |

###### Scenario: Feeder Line Device Operate Failure

Narrative

The Feeder Line Device sends an alarm to SCADA that is has failed to operate.  An example would be that the unit tries to open or close and is unable to do so because of a physical malfunction of the control linkage.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_Operate_failure FeederRecloser_Operate_failure FeederSwitch_Operate_failure FeederVR_Operate_failure |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Feeder Line Device Sensor Data Maintenance

Narrative

SCADA sends a command to the Feeder Line Device to issue a retrieval of the sensor data.  This can be used to determine physical conditions of the unit.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| SCADA | Feeder Line Device | < 5 seconds | 99.5% | 50 | FeederCBC_sensor_data_command FeederFault_Detector_sensor_data_cmd FeederRecloser_sensor_data_cmd FeederSensor_sensor_data_cmd FeederSwitch_sensor_data_cmd FeederVR_sensor_data_cmd |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 100 | FeederCBC_sensor_data_resp-data FeederFault_Detector_sensor_data_resp-data FeederRecloser_sensor_data_resp-data FeederSensor_sensor_data_resp-data FeederSwitch_sensor_data_resp-data FeederVR_sensor_data_resp-data |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Feeder Line Device Status Change Alert

Narrative

The Feeder Line Device sends a message to SCADA notifying the system that there has been a status change that’s either intentional or caused by a failure.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_status_change_alert FeederFault_Detector_status_change_alert FeederRecloser_status_change_alert FeederSensor_status_change_alert FeederSwitch_status_change_alert FeederVR_status_change_alert |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Feeder Line Device Sensor Data Maintenance

Narrative

SCADA sends a command to the Feeder Line Device to issue a retrieval of the status.  An example would be the present state (open/close) or active/deactive/functioning properly.

Business Objectives

| Originating Actor | Designation Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| SCADA | Feeder Line Device | < 5 seconds | 99.5% | 50 | FeederCBC_status_cmd FeederFault_Detector_status_cmd FeederRecloser_status_cmd FeederSensor_status_cmd FeederSwitch_status_cmd FeederVR_status_cmd |
| Feeder Line Device | SCADA | < 5 seconds | 99.5% | 100 | FeederCBC_status_resp-data FeederFault_Detector_status_resp-data FeederRecloser_status_resp-data FeederSensor_status_resp-data FeederSwitch_status_resp-data FeederVR_status_resp-data |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

#### Voltage and VAR Monitoring

##### Overview:  Voltage and VAR Management can reduce load while respecting given voltage tolerance (normal and emergency), conserve energy, reduce or eliminate overload in transmission lines, reduce or eliminate voltage violations on transmission lines, provide reactive power support for transmission/distribution bus, provide spinning reserve support, and/or minimize cost of energy.  For the distribution system, communications required for Voltage and VAR Management include monitoring of feeder line devices by polling or self-read at scheduled intervals, configuration or control of some of these feeder line devices, and can also include device deviations for operation outside of desired range.  Voltage and VAR Management can be Centralized with the most requirements for communications, or Distributed with the ability to coordinate between feeder line devices dependent on the amount of peer-to-peer communications.

- Substation Sensor (on feeder circuit breaker or feeder bus)

- Capacitor Bank Controller (CBC)

- Recloser

- Line Sensor

- Switch

- Voltage Regulator

- Customer Meter

###### Scenario: Device Deviation Alert

Narrative

The device sends an alarm to SCADA that is operating outside of its normal boundaries.  An example of this would be the system voltage drops under a predetermined level.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_deviation_alert FeederRecloser_deviation_alert FeederSensor_deviation_alert FeederSwitch_deviation_alert FeederVR_deviation_alert |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | CBC groupings not functional for mass operation. |

###### Scenario: Device Sensor Data- Poll

Narrative

SCADA sends a command to the device to issue a retrieval of the sensor data at scheduled intervals.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| SCADA | Device | < 5 seconds | 99.5% | 50 | FeederCBC_sensor_data_command FeederRecloser_sensor_data_cmd FeederSensor_sensor_data_cmd FeederSwitch_sensor_data_cmd FeederVR_sensor_data_cmd |
| Device | SCADA | < 5 seconds | 99.5% | 100 | FeederCBC_sensor_data_resp-data FeederRecloser_sensor_data_resp-data FeederSensor_sensor_data_resp-data FeederSwitch_sensor_data_resp-data FeederVR_sensor_data_resp-data |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Device Sensor Data- Push

Narrative

Self-read of sensor data at scheduled intervals.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Device | SCADA | < 5 seconds | 99.5% | 100 | FeederCBC_sensor_data_resp-data FeederRecloser_sensor_data_resp-data FeederSensor_sensor_data_resp-data FeederSwitch_sensor_data_resp-data FeederVR_sensor_data_resp-data |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

###### Scenario: Device Status Change Alert

Narrative

The device sends a message to SCADA notifying the system that there has been a status change that’s intentional.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Device | SCADA | < 5 seconds | 99.5% | 50 | FeederCBC_status_change_alert FeederRecloser_status_change_alert FeederSensor_status_change_alert FeederSwitch_status_change_alert FeederVR_status_change_alert |
| Totals | < 5 seconds | 99.5% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | Device groupings not functional for mass operation. |

#### Distribution System Demand Response DSDR

##### Overview:  Distribution System Demand Response is an operational mode that reduces the voltage on the Distribution Grid to help manage system load during periods of peak demand.  The parallel goal is to avoid violating any low voltage limits on the grid.

This use case encompasses four types of distribution feeder devices that operate within the parameters of demand response.  These devices include:

- Capacitor Banks

- Line Sensors

- Automated Feeder Switches

- Voltage Regulators

Below is an example architecture layout showing the Domain, Actors and Interfaces used in this use case.

Flow Diagram Figure XX

##### Communication:  The following examples show the communication paths that are implemented with the distribution devices above (shown as a field device in the diagram).  It is important to note that the communication strategy varies based upon the network that is chosen for back haul:

Communication Options Figure XX

##### Actors

| Name | Description |
| --- | --- |
| Automated Feeder Switches | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system. |
| Slave | This device provides the radio communication to the field device. |
| Master | This device provides radio communication between the Front End Processor, DMS and the field device. |
| Front End Processor | This device serves as the primary conduit for issuing commands from DMS/SCADA and receiving information from field devices deployed with in the Distribution network. |
| Distribution Management System and SCADA | Application responsible for collection of distributed information and issuance of Distribution Automation commands. |
| Voltage Regulators | These devices are deployed at critical points within the Distribution network for purposes of regulating voltage and providing system telemetry regarding the performance of the electric system. |
| Capacitor Bank | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. In addition, the device can be remotely controlled in order to increase voltage on a given segment of the Distribution network. |
| Line Sensor | A device capable of providing data on distribution and secondary line systems to show current, voltage, fault indication, loading or phase conditions. |
| Transformer Monitor | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |

##### Scenarios

###### Scenario: CBC Configuration

Narrative

The Capacitor Bank Controller may need to be configured remotely to allow it to function in different operating modes.  Some examples of these changes include adjusting time schedules for automatic turn on, voltage thresholds, and IP settings.  The communication would take place from DMS/SCADA though the network path to the end device.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | CBC | < 5 seconds | 99.5% | 500 | FeederCBC_new_config_cmd |
| CBC | DMS | < 5 seconds | 99.5% | 25 | FeederCBC_new_config_ack |
| Totals | < 10 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | CBC groupings not functional for mass operation. |

###### Scenario: CBC Operation (Open/Close)

Narrative

The CBC controls the capacitors by opening and closing breakers that feed onto the line system.  This is the primary function of the unit when it operates.  The operation is controlled by the control unit and can be directly operated from OMS based upon system conditions or other predefined requirements.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | CBC | < 5 seconds | 99.5% | 150 | FeederCBC_open_cmd FeederCBC_close_cmd |
| CBC | DMS | < 5 seconds | 99.5% | 25 | FeederCBC_open_ack FeederCBC_close_ack |
| Totals | < 10 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Customer voltage and VAR flow negatively impacted |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of system communication or improper operation |
| Service Providers |  |  |
| Transmission | X | CBC groupings not functional for mass operation. |

##### Scenario: CBC Data Read/Respond

Narrative

The CBC sends back data points related to both the device itself (housing temperature and breaker status), and line conditions (voltage, current, phase).  These data groupings are used to monitor the status of the device and also check for line conditions that may be used for analysis in the DMS as an additional node point.  The retrieval is initiated from DMS/SCADA and can be set for required intervals.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | CBC | < 2 seconds | 99.5% | 50 | FeederCBC_sensor_data_cmd |
| CBC | DMS | < 2 seconds | 99.5% | 100 | FeederCBC_sensor_data_resp-data |
| Totals | < 4 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution | X | Circuit feeder efficiency reduced |
| Markets |  |  |
| Operation | X | Loss of data causing DMS and other systems to analyze line conditions off of inaccurate or reduced information. Affects power flow studies. |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Sensor Configuration

Narrative

Line sensors that bring back data can be configured based upon the type of device and its role.  The configurations include network changes, rate of reads, and alarm thresholds for notification.  The changes are issued from DMS or a third party provider if the sensor operates on a proprietary network.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Sensor | < 5 seconds | 99.5% | 500 | FeederSensor_new_config_cmd |
| Sensor | DMS | < 5 seconds | 99.5% | 25 | FeederSensor_new_config_ack |
| Totals | < 10 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Outage restoration time increased |
| Distribution | X | Circuit feeder status inaccurate |
| Markets |  |  |
| Operation | X | Outage and fault location time increased |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Sensor Data Read/Respond

Narrative

Line sensors fall into two operational modes.  The first is exception based reporting where the device senses an event and initiates a message back to DMS.  The second mode is normal operation where some devices can be commanded to send interval data back on primary and secondary line conditions.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Sensor | < 2 seconds | 99.5% | 150 | FeederSensor_sensor_data_cmd |
| Sensor | DMS | < 2 seconds | 99.5% | 250 | FeederSensor_sensor_data_resp-data |
| Totals | < 4 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Outage restoration time increased |
| Distribution | X | Circuit feeder status inaccurate |
| Markets |  |  |
| Operation | X | Outage and fault location time increased |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario:  Switch Configuration

Narrative

Motor operated switch gear can be configured for several roles.  These units operate based upon a direct command from the system or in a team of switches that is set for automatic reconfiguration of a system based upon defined parameters.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Switch | < 5 seconds | 99.5% | 500 | FeederSwitch_new_config_cmd |
| Switch | DMS | < 5 seconds | 99.5% | 25 | FeederSwitch_new_config_ack |
| Totals | < 10 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | May experience unnecessary or lengthened outages |
| Distribution | X | Circuit remains in wrong configuration |
| Markets |  |  |
| Operation | X | Switch not set for optimal operation |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Switch Operation (Open/Close)

Narrative

DMS/SCADA issues a command to the switch to open or close because of a needed grid system change.  This can be used to help sectionalize a fault for circuit restoration or allow for a line reconfiguration off of a looped feed or neighboring circuit.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Switch | < 5 seconds | 99.5% | 150 | FeederSwitch_open_cmd FeederSwitch_close_cmd |
| Switch | DMS | < 5 seconds | 99.5% | 25 | FeederSwitch_open_ack FeederSwitch_close_ack |
| Totals | < 10 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | May experience unnecessary or lengthened outages |
| Distribution | X | Switch remains in wrong position causing loss of power or added load on a circuit |
| Markets |  |  |
| Operation | X | Operation Failure |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Switch Data Read/Respond

Narrative

Motor operated switches are capable of sending information including device status, breaker position, temperature, and voltage information.  The data package can include information about the switch or the line itself (with installed sensors).  This information is used in DMS to determine circuit configurations and line conditions.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Switch | < 2 seconds | 99.5% | 50 | FeederSwitch_sensor_data_cmd |
| Switch | DMS | < 2 seconds | 99.5% | 100 | FeederSwitch_sensor_data_resp-data |
| Totals | < 4 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution | X | Failure to communicate and know switch status |
| Markets |  |  |
| Operation | X | Unable to make decisions based upon real time information |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario:  Voltage Regulator Configuration

Narrative

Voltage regulators can be configured to operate and raise or lower levels based upon set thresholds on the device.  The device can be set to operate independently or by direct control from DMS.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | < 5 seconds | 99.5% | 500 | FeederVR_new_config_cmd |
| Voltage Regulator | DMS | < 5 seconds | 99.5% | 25 | FeederVR_new_config_ack |
| Totals | < 10 seconds | 96% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Negative impact on secondary voltage levels |
| Distribution | X | Line not conditioned properly to meet 120v base |
| Markets |  |  |
| Operation |  |  |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Voltage Regulator Step Operation

Narrative

The Voltage Regulator has a series of steps that can be raised and lowered to change the output voltage on the primary line system.  These devices are used to help keep the voltage within the operating guidelines of the system.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | < 2 seconds | 99.5% | 250 | FeederVR_step_up_cmd FeederVR_step_down_cmd |
| Voltage Regulator | DMS | < 2 seconds | 99.5% | 25 | FeederVR_step_up_ack FeederVR_step_down_ack |
| Totals | < 4 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer | X | Negative impact on secondary voltage levels |
| Distribution | X | Line not conditioned properly to meet 120v base |
| Markets |  |  |
| Operation |  |  |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Voltage Regulator Data read/Respond

Narrative

The voltage regulator can have sensors built into the device that act as another node point on the line for retrieving feeder data.  This data can be used with other devices to make a clear picture of the grid system to an operator or an automatic DMS setup.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | < 2 seconds | 99.5% | 150 | FeederVR_sensor_data_cmd |
| Voltage Regulator | DMS | < 2 seconds | 99.5% | 1000 | FeederVR_sensor_data_resp-data |
| Totals | < 4 seconds | 99% |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution | X | System voltage levels are not maintained properly. |
| Markets |  |  |
| Operation | X | System does not receive real time updates of line conditions |
| Service Providers |  |  |
| Transmission |  |  |

##### Scenario: Distributed Device Operations

Narrative

Each of the devices above (except sensors) can operate in a distributed mode if programmed to do so by the utility.  The device will respond to DMS with an indication of the action that has been performed remotely.

Business Objectives

| Originating Actor | Destination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| CBC | DMS | < 5 seconds | 99.5% | 25 | FeederCBC_open_ack |
| CBC | DMS | < 5 seconds | 99.5% | 25 | FeederCBC_close_ack |
| Voltage Regulator | DMS | < 5 seconds | 99.5% | 25 | FeederVR_step_up_ack |
| Voltage Regulator | DMS | < 5 seconds | 99.5% | 25 | FeederVR_step_down_ack |
| Switch | DMS | < 5 seconds | 99.5% | 25 | FeederSwitch_open_ack |
| Switch | DMS | < 5 seconds | 99.5% | 25 | FeederSwitch_close_ack |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |
| Bulk Generation |  |  |
| Customer |  |  |
| Distribution | X | Decision analysis would be performed on inaccurate data and improper line configurations |
| Markets |  |  |
| Operation | X | System is not aware of the actual status and configuration on the circuits. |
| Service Providers |  |  |
| Transmission |  |  |

#### Line Segmentation

Line segmentation is the concept of dynamically reconfiguring loop feeders to restore the maximum number of customers after a fault has caused a section of the gird (i.e. a feeder segment) to be out of service.

#### Distributed Energy Resources

Distributed Energy Resources, also called on-site generation, dispersed generation, embedded generation, decentralized generation, decentralized energy or distributed generation, generates electricity from many small energy sources.

### Actors

| Actor | Description |
| --- | --- |
| Automated Feeder Switches | These devices are deployed at critical points with in the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system. |
| Slave | This device provides the radio communication to the Automated Feeder switch. |
| Master | This device provides radio communication between the Front End Processor, DMS and the automated feeder switch. |
| Front End Processor | This device serves as the primary conduit for issuing commands from DMS/SCADA and receiving information from field devices deployed with in the Distribution network. |
| Distribution Management System and SCADA | Application responsible for collection of distributed information and issuance of Distribution Automation commands. |
| Automated Feeder Switches | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system. |
| Voltage Regulators | These devices are deployed at critical points within the Distribution network for purposes of regulating voltage and providing system telemetry regarding the performance of the electric system. |
| Capacitor Bank | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. In addition, the device can be remotely controlled in order to increase voltage on a given segment of the Distribution network. |
| Fault Current Indicator | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Transformer Monitor | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Voltage and Current sensor | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Network Protector | An Intelligent Electronic Device that provides electronic analog performance information, status and fault information. |
| Throw Over Switch | A device that provides electronic analog status and fault information. |

Table 18 - Distribution Automation Actor Descriptions

### Automated Feeder / Re-closer Switching

#### Objective

The process involves the automatic isolation and notification of faults with in the Distribution electric system.  The process requires close orchestration between the DMS system and automated feeder / re-closer switching devices deployed with in the Distribution network.

#### Actors

| Actor | Role |
| --- | --- |
| Automated Feeder Switches | Primary and Secondary |
| Slave | Secondary |
| Master | Secondary |
| Front End Processor | Primary |
| Distribution Management System and SCADA | Primary |

Table 19 - Actors Automated Feeder Switching

#### Applicable Distribution Applications

| Source | Destination | Payload | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Recloser | Status Request | Y | Y |  |  | Y |  |
| DMS | Recloser | Sensor Data request | Y | Y |  |  | Y |  |
| DMS | Recloser | Command – Step UP | Y |  |  |  | Y |  |
| DMS | Recloser | Command – Step Down | Y |  |  |  | Y |  |
| DMS | Recloser | New Config | Y |  | Y |  | Y |  |
| Recloser | DMS | Status Change | Optional | Y |  |  |  |  |
| Recloser | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Recloser | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Recloser | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 20 - Applicable Distribution Applications

#### Latency Requirements - Switching

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| AF Switch 1 | AF Switch 2 | Event Driven | 2 Seconds | HIGH |
| AF Switch 2 | AF Switch 1 | Event Driven | 2 Seconds | HIGH |
| AF Switch 1 | Master | Event Driven | 2 Seconds | HIGH |
| AF Switch 2 | Master | Event Driven | 2 Seconds | HIGH |
| Master | AF Switch 1 | Event Driven | 2 Seconds | HIGH |
| Master | AF Switch 2 | Event Driven | 2 Seconds | HIGH |
| DMS | AF Switch 1 | Event Driven | ~5 Seconds | HIGH |
| DMS | AF Switch 2 | Event Driven | ~5 Seconds | HIGH |
| AF Switch 1 | DMS | Event Driven | ~5 Seconds | HIGH |
| AF Switch 2 | DMS | Event Driven | ~5 Seconds | HIGH |

Table 21 - Latency requirements AFS operation

#### Latency Requirements - Telemetry

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | AF Switch 1 | 5 Second Interval | ~5 Seconds | HIGH |
| DMS | AF Switch 2 | 5 Second Interval | ~5 Seconds | HIGH |

Table 22 - Latency requirements Automated Feeder Switch Telemetry

#### Process Flow

Figure 9 - Information flow AFS automated operation

#### Included Processes

##### Manual Switch Operation

Figure 10 - Information flow AFS Manual Switch Operation

##### Switch Monitoring and Diagnostics

Figure 11 - Information flow AFS monitoring and diagnostics

##### Switch Configuration Change

Figure 12 - Information flow AFS manual DNP configuration change

##### Switch Operation and Configuration Change

Figure 13 - Information flow manual switch operation and DNP configuration change

##### Switch to Switch Fault Detection

This process involves notification and interaction with devices in the event a fault is identified to have occurred in between deployed DA switches.

##### Switch to Breaker Fault Detection

This process involves notification and interaction with devices in the event a fault is identified to have occurred in between a deployed DA switch and the substation.

### Voltage Regulator

#### Objective

The process involves the automatic and manual operation of voltage regulators to improve the voltage characteristics of any particular segment of the distribution network.   The process requires close orchestration between the DMS system and voltage regulation devices deployed with in the Distribution network.

#### Actors

| Actor | Role |
| --- | --- |
| Voltage Regulators | Primary |
| Slave | Secondary |
| Master | Secondary |
| Front End Processor | Primary |
| Distribution Management System and SCADA | Primary |

Table 23 - Actors Voltage Regulator Operation

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Voltage Regulator | Status Request | Y | Y |  |  |  |  |
| DMS | Voltage Regulator | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Voltage Regulator | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Voltage Regulator | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Voltage Regulator | New Config | Y |  | Y | Y | Y | Y |
| Voltage Regulator | DMS | Status Change | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Voltage Regulator | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 24 - Applicable Distribution Applications

#### Latency Requirements - Operation

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | Event Driven | 5 Seconds | High |
| Voltage Regulator | DMS | Event Driven | 5 Seconds | High |
| Master | Voltage Regulator | Event Driven | 2 Seconds | High |
| Voltage Regulator | Master | Event Driven | 2 Seconds | High |

Table 25 - Latency requirements Voltage Regulator Operation

#### Latency Requirements - Telemetry

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Voltage Regulator | 5 Second Interval | ~5 Seconds | HIGH |

Table 26 - Latency requirements Voltage Regulator Telemetry

#### Process Flow

Figure 14 - Information flow Voltage Regulator operation

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Capacitor Bank Control

#### Objective

The objective is to remotely operate and poll capacitor banks for purposes of modifying the voltage and power quality on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of capacitor banks.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Capacitor Bank | Primary |

Table 27 - Actors Capacitor Banks

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Capacitor Bank | Status Request | Y | Y |  |  |  |  |
| DMS | Capacitor Bank | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Capacitor Bank | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Capacitor Bank | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Capacitor Bank | New Config | Y |  | Y | Y | Y | Y |
| Capacitor Bank | DMS | Status Change | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Alarm Condition | Optional | Y |  |  |  |  |
| Capacitor Bank | DMS | Device Failure | Optional | Y |  |  |  |  |

Table 28 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Capacitor Bank | Event Driven | 5 Seconds | High |
| Capacitor Bank | DMS | Event Driven | 5 Seconds | High |
| Master | Capacitor Bank | Event Driven | 2 Seconds | High |
| Capacitor Bank | Master | Event Driven | 2 Seconds | High |

Table 29 - Latency requirements Capacitor Bank Operation

#### Process Flow

Figure 15 - Information flow Capacitor Bank Control

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

##### Capacitor Bank Monitoring

Figure 16 - Information flow Capacitor Bank Monitoring

### Fault Current Indicator

#### Objective

The objective is to remotely poll and collect information from fault current indicators on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of fault current indicators.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Fault Current Indicator | Primary |

Table 30 - Actors Fault Current Indicator

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Fault Current Indicator | Status Request | Y |  |  |  | Y |  |
| DMS | Fault Current Indicator | Sensor Data request | Y |  |  |  | Y |  |
| DMS | Fault Current Indicator | New Config | Y |  |  |  | Y |  |
| Fault Current Indicator | DMS | Deviation Alert | Optional | Y |  |  | Y |  |
| Fault Current Indicator | DMS | Alarm Condition | Optional | Y |  |  | Y |  |

Table 31 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | Event Driven | 5 Seconds | High |
| Slave | DMS | Event Driven | 5 Seconds | High |
| Master | Slave | Event Driven | 2 Seconds | High |
| Slave | Master | Event Driven | 2 Seconds | High |

Table 32 - Latency requirements Fault Current Indicator

#### Process Flow

Figure 17 - Information flow Fault current Indicator

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Transformer Monitoring

#### Objective

The objective is to remotely poll and collect information from transformer monitors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of transformer monitors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Transformer Monitor | Primary |

Table 33 - Actors Transformer Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Transformer Monitor | Status Request | Y | Y |  |  |  |  |
| DMS | Transformer Monitor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Transformer Monitor | New Config | Y |  | Y | Y | Y | Y |
| Transformer Monitor | DMS | Status Change | Optional | Y |  |  |  |  |
| Transformer Monitor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Transformer Monitor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 34 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 15 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | NA | 10 Seconds | Medium |
| Master | Slave | NA | 5 Seconds | Medium |
| Slave | Master | NA | 5 Seconds | Medium |

Table 35 – Latency requirements Transformer Monitoring

#### Process Flow

Figure 18 - Information flow Transformer Monitor

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Voltage and Current Sensors

#### Objective

The objective is to remotely poll and collect information from voltage and current sensors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of voltage and current sensors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Voltage and Current sensor | Primary |

Table 36 - Actors Voltage and Current Sensors

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Sensor | Status Request | Y | Y |  |  |  |  |
| DMS | Sensor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Sensor | New Config | Y |  | Y | Y | Y | Y |
| Sensor | DMS | Status Change | Optional | Y |  |  |  |  |
| Sensor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Sensor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 37 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Second Interval | 10 Seconds | Medium |
| Slave | DMS | NA | 10 Seconds | Medium |
| Master | Slave | NA | 5 Seconds | Medium |
| Slave | Master | NA | 5 Seconds | Medium |

Table 38 -Latency requirements Amp / voltage sensor

#### Process Flow

Figure 19 - Information flow Amp / Voltage Sensor

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Network Protection Monitoring

#### Objective

The objective is to remotely poll and collect information from network protection monitors on a particular segment of distribution.  The intent of this use case is to document the process for automated and manual operation of network protection monitors.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Network Protector | Primary |

Table 39 - Actors Network Protector Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Switch | Status Request | Y | Y |  |  | Y |  |
| DMS | Switch | Sensor Data request | Y | Y |  | Y | Y |  |
| DMS | Switch | Command – Step UP | Y |  | Y | Y | Y | Y |
| DMS | Switch | Command – Step Down | Y |  | Y | Y | Y | Y |
| DMS | Switch | New Config | Y |  |  |  | Y |  |
| Switch | DMS | Status Change | Optional | Y |  |  | Y |  |
| Switch | DMS | Deviation Alert | Optional | Y |  |  | Y |  |
| Switch | DMS | Alarm Condition | Optional | Y |  |  | Y |  |
| Switch | DMS | Device Failure | Optional | Y |  |  | Y |  |

Table 40 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | Event Driven | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 41 - Latency Requirements Network Protector Monitoring

#### Process Flow

Figure 20 - Information flow Network Protector

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Throw Over Switch Monitoring

#### Objective

The objective is to remotely poll and collect information from throw over switch monitors on a particular segment of distribution.  The intent of this use case is to document the process for monitoring throw over switches.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| Throw Over Switch | Primary |

Table 42 - Actors Throw Over Switch Monitoring

#### Applicable Distribution Applications

| Source | Destination | Transaction | Acknowledged or replied | Distribution application |
| --- | --- | --- | --- | --- |
|  |  |  |  | Maintenance | Voltage &Var Monitoring | DSDR | Line Seg | Distributed Energy Resources |
| DMS | Switch Sensor | Status Request | Y | Y |  |  |  |  |
| DMS | Switch Sensor | Sensor Data request | Y | Y |  | Y |  |  |
| DMS | Switch Sensor | New Config | Y |  | Y | Y | Y | Y |
| Switch Sensor | DMS | Status Change | Optional | Y |  |  |  |  |
| Switch Sensor | DMS | Deviation Alert | Optional | Y |  |  |  |  |
| Switch Sensor | DMS | Alarm Condition | Optional | Y |  |  |  |  |

Table 43 - Applicable Distribution Applications

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 44 - Latency Requirements Throw Over Switch Monitoring

#### Process Flow

Figure 21 - Information flow Throw Over Switch

#### Included Processes

##### Alerts and Alarms

##### Status Change and System Conditions

### Health Checks

#### Objective

The objective is to remotely poll and collect information health information from distribution equipment on a particular segment of distribution.

#### Actors

| Actor | Role |
| --- | --- |
| Dispatch Operator | Primary |
| Distribution Management System and SCADA | Primary |
| Front End Processor | Secondary |
| Master | Secondary |
| Repeaters | Secondary |
| Slave | Secondary |
| RTU | Primary |

Table 45 – Actors Device Health Check

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| DMS | Slave | 5 Minute Interval | 10 Seconds | Medium |
| Slave | DMS | Event Driven | 10 Seconds | Medium |
| Master | Slave | Event Driven | 5 Seconds | Medium |
| Slave | Master | Event Driven | 5 Seconds | Medium |

Table 46 - Latency Requirements Device Health Check

#### Process Flow

Figure 22 - Information flow Health check

### Power Quality Event (Kelly)

#### Objective

The objective is to collect alarms from the meter that occur when there is a out of state or passed a threshold condition on the meter.  Power quality event are disturbance oriented by nature, leading / lagging power.  In most cases the events will be as result of excessive steady state voltage variation, unbalance in energy flow, harmonics on the line, sags, swells, oscillatory.

#### Actors

| Actor | Description | Role |
| --- | --- | --- |
| Meter Data Management System | The MDMS is the application responsible for coordinating the billing of AMI data. MDMS often interact with CIS, as well as other systems, to automate customer and billing functions with the Smart Grid. |  |
| AMI Head End | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |  |
| Data Aggregation Point | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters. |  |
| Smart Meter – AMI Interface | This is the interface utilized to communicate directly between the Smart Meter and the AMI system. This interface is used to allow utilities and third parties to communicate with the meter via the AMI system. |  |

Table 47 - Metering Power Quality Actors

#### Latency Requirements

| Source | Destination | Frequency | Response Time | Priority |
| --- | --- | --- | --- | --- |
| Smart Meter | DAP | Event Driven | <30 sec | High |
| DAP | AMI Head End | Event Driven | <30 sec | High |
| AMI Head End | MDMS | Event Driven | <30 sec | High |

Table 48 - Latency Requirements

#### Process Flow

Figure 23 - Process Flow

#### Included Processes

## Pricing TOU / RTP/ CPP

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. |
| Cust. EMS | A customer owned energy management system used to manage energy with a premises. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| DSM - REPi | Demand Side Management - Retail Energy Provider; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| DSM - Utility | Demand Side Management - Utility; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| ESI - 3rd Party | An ESI, owned by the Customer and not provided by the Utility, which enables secure interactions between HAN Devices Registered on its network and the service provider e.g. REP. The 3rd Party ESI functionality may reside in the Customer EMS or customer's |
| ESI - In Meter | An ESI, owned by the Utility and resides in the Utility meter, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. |
| ESI - Utility | An ESI, owned by the Utility, which enables secure interactions between HAN Devices Registered on its network and the Utility AMI. The Utility ESI functionality may reside in the Customer EMS or customer broadband router. |
| EVSE / EUMD | Electric Vehicle Supply Equipment / End Use Metering Device |
| Internet / Extranet gateway(s) - REPi | These are gateways used to connect internal utility networks with external networks. |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| IPD | In Premise Display |
| LMS - REPi | Load management system |
| LMS - Utility | Load management system - System that controls load by sending messages directly to device (e.g. On/Off) |
| Load Cntl Device | A device used within the customer domain for load management (e.g. Air conditioning, etc) |
| PCT | A device within the premise that has communication capabilities and controls heating, ventilation and cooling systems. |
| PHEV | Plug-in Hybrid Electric Vehicles - Cars or other vehicles that draw electricity from batteries to power an electric motor for vehicle propulsion. PHEVs also contain an internal combustion engine. |
| Smart Appliance | A white good or household appliance, that has HAN communication capability and is capable of receiving signals from authorized parties (e.g. Utility, Service Provider, EMS, Consumer, etc.) and of adjusting its operational mode based on Consumer preference |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Security Management

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Service Switch

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| 2-Way Meter - Electr | A bi-directional communication device used to perform measurement of electrical energy usage for residential use. |
| --- | --- |
| 2-Way Meter - Gas | A bi-directional communication device used to perform measurement of gas consumption for residential use. |
| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| CIS/Billing - Utility | A utility billing system used for reconcilling customer payments for electricity usage. This system may also be used for manageing vendors of electricity generation. |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| DSM - Utility | Demand Side Management - Utility; A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| LMS - Utility | Load management system - System that controls load by sending messages directly to device (e.g. On/Off) |
| MDMS | The application responsible for the collection and retrieval of all relevant customer information for purposes of billing and facilitating interaction. |
| NMS | A system or series of systems that are utilized to operate and manage utility assets that interact on any given network. These assets are comprised of both hardware and software components that require ongoing monitoring and management. |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Transmission Automation

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

## Volt/VAR Management –Centralized

### Overview

#### Reference Architecture with Domains, Actors and Interfaces

#### Possible communication paths

### Actors

| AMI Head-End(j) | The AMI head end is responsible for the operation and coordination of AMI system components. It represents the central nervous system of the AMI system. |
| --- | --- |
| DAC - sub | Distribution Application Control system hosted in a Distribution Substation to run a specific Distrbution application |
| DAPjm | This is the Data Aggregation Point on the NAN. It is essentially the point of convergence for all communication between SG devices and utility back office systems. In this specific use case it provides a communication conduit for AMI Smart Meters.The su |
| Distr. SCADA FEP | Distribution Supervisory Control and Data Acquisition Front End Processor |
| DMS | Distribution Management System - A system that monitors, manages and controls the electric distribution system. |
| FAN gateway - field | Field Area Network gateway device located in the field, that provides the interface between the Feeder Line device communication modules and the Wide Area Network connection. |
| FAN gateway - sub | Field Area Network gateway device located in the substation, that provides the interface between the Feeder Line device communication modules and the Substation network connection. |
| Feeder Cap Bank | This is a device used to add capacitance as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Feeder Recloser | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing |
| Feeder Regulator | This device is in effect an adjustable ratio transformer positioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| Feeder Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Feeder Switch | These devices are deployed at critical points within the Distribution network for purposes of isolating electric faults and providing system telemetry regarding the performance of the electric system |
| Internet / Extranet gateway(s) - Utility | These are gateways used to connect internal utility networks with external networks. |
| RTU | Remote Terminal Unit - Aggregator of multiple serialized devices to a common communications interface |

### Scenarios

#### Scenario: X

Narrative

Business Objectives

| Originating Actor | Desination Actor | Latency | Reliability | Payload Size | Payload Name |
| --- | --- | --- | --- | --- | --- |
| Totals |  |  |  |  |

Implications and Rationale

| Functional Domain | Expected Potential Impact | Rationale |
| --- | --- | --- |

Appendix

## Acronyms and Abbreviations

| AC | Alternating Current |
| --- | --- |
| AMI | Advanced Metering Infrastructure |
| AMS | Asset management system |
| ASAP-SG | Advanced Security Acceleration Project-Smart Grid |
| B2B | Business to Business |
| BAN | Business Area Network |
| CIM | Common Information Model. |
| CIP | Critical Infrastructure Protection |
| CIS | Customer Information System |
| CSWG | Cyber Security Working Group |
| DA | Distribution Automation |
| DAC | Distribution Application Controller |
| DAP | Data Aggregation Point |
| DC | Direct Current |
| DER | Distributed Energy Resources e.g. solar, wind, photovoltaic |
| DHS | Department of Homeland Security |
| DMS | Distribution Management System |
| DNP | Distributed Network Protocol |
| DOE | Department of Energy |
| DOMA | Distribution Operations Model and Analysis |
| DR | Demand Response |
| DSDR | Distribution Systems Demand Response |
| DSM | Demand Side Management |
| EMS | Energy Management System |
| EPRI | Electric Power Research Institute |
| ES | Electric Storage |
| ESB | Enterprise Service Bus |
| ESI | Energy Services Interface |
| ET | Electric Transportation |
| EUMD | End Use Measurement Device |
| EV/PHEV | Electric Vehicle/Plug-in Hybrid Electric Vehicles |
| EVSE | Electric Vehicle Supply Equipment |
| FAN | Field Area Network |
| FCC | Federal Communications Commission |
| FEP | Front End Processor |
| FERC | Federal Energy Regulatory Commission |
| FIPS | Federal Information Processing Standard Document |
| FLIR | Fault Location, Isolation, Restoration |
| G&T | Generations and Transmission |
| GAPP | Generally Accepted Privacy Principles. |
| GIS | Geographic Information System |
| GL | General Ledger |
| GPRS | General Packet Radio Service |
| HAN | Home Area Network |
| HMI | Human-Machine Interface |
| HV | High Voltage (in definition) |
| HVAC | Heating, Ventilating, and air conditioning (shown in figure) |
| I2G | Industry to Grid |
| IEC | International Electrotechnical Commission |
| IED | Intelligent Electronic Device |
| IHD | In-home Display |
| IPD | In Premise Display |
| ISA | International Society of Automation |
| ISO | Independent System Operator |
| ISO/IEC27001 | International Organization for Standardization/International Electrotechnical Commission Standard 27001. |
| IT | Information Technology |
| LAN | Local Area Network |
| LMS | Load management system |
| LMS/DRMS | Load Management System/ Distribution Resource Management System |
| LV | Low voltage (in definition) |
| MDMS | Meter Data Management System |
| MFR | Multi-Feeder Reconnection |
| MSW | Meter service switch |
| MV | Medium voltage (in definition) |
| NAN | Neighborhood Area Network |
| NERC | North American Electric Reliability Corporation |
| NIPP | National Infrastructure Protection Plan |
| NIST | National Institute of Standards and Technology |
| NISTIR | NIST Interagency Report |
| NMS | Network Management system |
| ODW | Operational Data Warehouse |
| OMS | Outage Management System |
| OWASP | Open Web Application Security Project |
| PAN | Premise Area Network - synonymous for HAN |
| PAP | Priority Action Plan |
| PCT | Programmable Communicating Thermostat |
| PEV | Plug-In Electric Vehicle |
| PI | Process Information |
| PIA | Privacy Impact Assessment. . |
| PII | Personally Identifying Information |
| R&D | Research and Development |
| REP | Retail Energy Provider |
| RTO | Regional Transmission Operator |
| RTU | Remote Terminal Unit |
| SCADA | Supervisory Control and Data Acquisition |
| SCE | Southern California Edison |
| SGIP | Smart Grid Interoperability Panel |
| SGIP-CSWG | SGIP – Cyber Security Working Group |
| SP | Special Publication |
| SSP | Sector-Specific Plans |
| T/FLA | Three/Four Letter Acronym |
| TXT | Text Message or Messaging |
| VAR | Volt-Amperes Reactive |
| VVWS | Volt-VAR-Watt System |
| WAMS | Wide-Area Measurement System |
| WAN | Wide Area Network |
| WASA | Wide Area Situational Awareness |
| WLAN | Wireless Local Area Network |
| WMS | Work Management System |

## Definitions

| Actor | A generic name for devices, systems, or programs that make decisions and exchange information necessary for performing applications: smart meters, solar generators, and control systems represent examples of devices and systems. |
| --- | --- |
| Anonymize | A process of transformation or elimination of PII for purposes of sharing data |
| Aggregation | Practice of summarizing certain data and presenting it as a total without any PII identifiers |
| Aggregator | A mechanism for collecting like streams of data or metering for use as a single figures by upstream systems. |
| Applications | Tasks performed by one or more actors within a domain. |
| Asset Management System | A system(s) of record for assets managed in the Smart Grid. Management context may change(e.g. financial, network) |
| Bulk Generation | The generators of electricity in bulk quantities. May also store energy for later distribution (from NIST Smart Grid Framework and Roadmap). |
| Capacitor Bank | This is a device used to add reactive power as needed at strategic points in a distribution grid to better control and manage VARs and thus the Power Factor and they will also affect voltage levels. |
| Common Information Model | A structured set of definitions that allows different Smart Grid domain representatives to communicate important concepts and exchange information easily and effectively. |
| Common Web Portal | Web interface for Regional Transmission Operator, customers, retail electric providers and transmission/distribution service provider to function as a clearing house for energy information. Commonly used in deregulated markets. |
| Customer | The end users of electricity. May also generate, store, and manage the use of energy. Traditionally, three customer types are discussed, each with its own domain: residential, commercial, and industrial (from NIST Smart Grid Framework and Roadmap). |
| Data Aggregation Point | This device is a logical actor that represents a transition in most AMI networks between Wide Area Networks and Neighborhood Area Networks. (e.g. Collector, Cell Relay, Base Station, Access Point, etc) |
| De-identify | A form of anonymization that does not attempt to control the data once it has had PII identifiers removed, so it is at risk of re-identification. |
| Demand Side Management | A system that co-ordinates demand response / load shedding messages indirectly to devices (e.g. Set point adjustment) |
| Distribution | The distributors of electricity to and from customers. May also store and generate electricity. |
| Distribution Management System | A system that monitors, manages and controls the electric distribution system. |
| Distribution Systems Demand Response | A system used to reduce electric distribution load during peak demand. Strictly used for Distribution systems only. |
| Domain | A high-level grouping of organizations, buildings, individuals, systems, devices, or other actors with similar objectives and relying on—or participating in— similar types of applications (from NIST Framework and Roadmap) |
| Electric Vehicle/Plug-in Hybrid Electric Vehicles | Cars or other vehicles that draw electricity from batteries to power an electric motor for vehicle propulsion. PHEVs also contain an internal combustion engine. |
| Energy Services Interface | Provides security and, often, coordination functions that enable secure interactions between relevant Home Area Network Devices and the Utility. Permits applications such as remote load control, monitoring and control of distributed generation, in-home display of customer usage, reading of non-energy meters, and integration with building management systems. Also provides auditing/logging functions that record transactions to and from Home Area Networking Devices. |
| Enterprise Service Bus | The Enterprise Service Bus consists of a software architecture used to construct integration services for complex event-driven and standards-based messaging for data exchange. The ESB is not limited to a specific tool set, rather it is a defined set of integration services. |
| Fault Detector | A device used to sense a fault condition on an electrical circuit and can be used to provide a local and/or remote indication of the fault. |
| Field Force | Employee working in the service territory that may be working with Smart Grid devices. |
| GAPP | Generally Accepted Privacy Principles. Privacy principles and criteria developed and updated by the AICPA and Canadian Institute of Chartered Accountants to assist organizations in the design and implementation of sound privacy practices and policies. |
| Home Area Network | A network of energy management devices, digital consumer electronics, signal-controlled or enabled appliances, and applications within a home environment that is on the premise side of the electric meter. In-premise communication system (OpenHAN 2.0) |
| ISO/IEC27001 | An auditable international standard that specifies the requirements for establishing, implementing, operating, monitoring, reviewing, maintaining and improving a documented Information Security Management System within the context of the organization's overall business risks. It uses a process approach for protection of critical information |
| Last Gasp | Concept of an energized device within the Smart Grid detecting power loss and sending a broadcast message of the event prior to complete power loss. |
| Load Management System | System that controls load by sending messages directly to device (e.g. On/Off) |
| Low Voltage Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) at a low voltage customer delivery point. |
| Markets | The operators and participants in electricity markets (from NIST Smart Grid Framework and Roadmap) |
| Medium Voltage Sensor | A device used to measure and report electrical properties (such as voltage, current, phase angle or power factor, etc.) on a medium voltage distribution line. |
| Motorized Switch | A load break device under remote control that can be used to open or close a circuit. |
| Neighborhood Area Network | A network comprised of all communicating components within a distribution domain. |
| Network Management System | A system that manages Fault, Configuration, Auditing/Accounting, Performance and Security of the communication network. This system is exclusive from the electrical network. |
| Operations | The managers of the movement of electricity (from NIST Smart Grid Framework and Roadmap). |
| Outage Management System | A system that receives out power system outage notifications and correlates the geographic location of the power outage |
| Personally Identifying Information | (PII) Information that reveals details, either explicitly or implicitly, about a specific individual’s household dwelling or other type of premises. This is expanded beyond the normal "individual" component because there are serious privacy impacts for all individuals living in one dwelling or premise. This can include items such as energy use patterns or other types of activities. The pattern can become unique to a household or premises just as a fingerprint or DNA is unique to an individual. |
| Phase Measuring Unit | A device capable of measuring the phase of the voltage or current waveform relative to a reference. |
| Power Factor | A dimensionless quantity that relates to efficiency of the electrical delivery system for delivering real power to the load. Numerically, it is the Cosine of the phase angle between the voltage and current waveforms. The closer the power factor is to unity the better the inductive and capacitive elements of the circuit are balanced and the more efficient the system is for delivering real power to the load(s). |
| Privacy Impact Assessment | A process used to evaluate the possible privacy risks to Personally Identifying Information, in all forms, collected, transmitted, shared, stored, disposed of, and accessed in any other way, along with the mitigation of those risks at the beginning of and throughout the life cycle of the associated process, program or system |
| Programmable Communicating Thermostat | A device within the premises that has communication capabilities and controls heating, ventilation and cooling systems. |
| Recloser (non-Team) | A device used to sense fault conditions on a distribution line and trip open to provide protection. It is typically programmed to automatically close (re-close) after a period of time to test if the fault has cleared. After several attempts of reclosing it can be programmed to trip open and stop trying to reclose until reset either locally or under remote control. |
| Recloser (Team) | A device that can sense fault conditions on a distribution line and to communicate with other related reclosers (the team) to sectionalize the fault and provide a coordinated open/close arrangement to localize the effect of the fault. |
| Regional Transmission Operator | A Regional Transmission Organization (RTO) is an organization that is established with the purpose of promoting efficiency and reliability in the operation and planning of the electric transmission grid and ensuring non-discrimination in the provision of electric transmission services based on specific required/demonstrable characteristics and functions. |
| Remote Terminal Unit | Aggregator of multiple serialized devices to a common communications interface |
| Service Providers | The organizations providing services to electrical customers and utilities (from NIST Smart Grid Framework and Roadmap). |
| Sub Meter | Premise based meter used for Distributed Energy Resources and PHEV installed downline from the utility’s meter. This device may be revenue grade. |
| Substation Controller | Distributed processing device that has supervisory control or coordinates information exchanges from devices within a substation from a head end system. |
| Transformer (MV-to-LV) | A standard point of delivery transformer. In the Smart Grid context is it assumed there will be a need to measure some electrical or physical characteristics of this transformer such as voltage (high and/or low side) current, MV load, temperature, etc. |
| Transmission | The carriers of bulk electricity over long distances. May also store and generate electricity. |
| Use Case | Use cases are a systems engineering tool for defining a system’s behavior from the perspective of users. In effect, a use case is a story told in structure and detailed steps—scenarios for specifying required usages of a system, including how a component, subsystem, or system should respond to a request that originates elsewhere. |
| Voltage Regulator | This device is in effect an adjustable ratio transformer positioned at strategic points in a distribution grid and is utilized to better manage and control the voltage as it changes along the distribution feeder. |
| VAR – Volt-Amperes Reactive; | In an AC power system the voltage and current measured at a point along the delivery system will often be out of phase with each other as a result the combined effects of the resistive and reactive (i.e. the capacitance and inductive) characteristics of the delivery system components and the load. The phase angle difference at a point along the delivery system is an indication of how well the inductive and capacitive effects are balanced at that point. The real power passing that point is the product of the magnitude of the Voltage and Current and the Cosine of the angle between the two. The VAR parameter is the product of the magnitude of the Voltage and Current and the Sine of the angle between the two. The magnitude of the VAR parameter is an indication of the phase imbalance between the voltage and current waveforms. |
| Web Portal | Interface between energy customers and the system provider. Could be the utility or third party |

## Alternative / Multiple Communication Paths

Appendix – Alternative / Multiple Communication Paths

Referring to the Reference Diagram with multiple data communication paths, how do we select which ones are appropriate and applicable to the deployment being studied or modeled? If one focuses on a very simplistic example of the CIS/Billing – Utility to 2Way-Meter data, two communications path options and one deployment decision need to be made: (refer to following diagram). Note that this example does not contain all of the communication paths possible between the CIS/Billing – Utility to 2Way-Meter. For the full set of communication path options and decisions, refer to Reference Diagram and the decision details later in this appendix.

Figure 5.4-1 Alternative / Multiple Communication Paths – Reference Diagram Snippet

Three different ways of documenting these communication path options and deployment decisions are presented in this appendix:

- Graphical Parsing of the Unique From / To Actor Pairing

- Payload Requirement Set Data Flow Ref Pseudo Code

- Communication Path and Deployment Decisions Graphical Pseudo Code

Graphical Parsing of the Unique From / To Actor Pairing

This approach documents all the unique combinations of traversing the available communication paths from one end of a payload requirement set’s from/to actor pairing to the other end point actor, using the Reference Diagram as the baseline. The following figure illustrates this process for a very simplistic example of the CIS / Billing – Utility communications paths with the 2Way-Meter actors, but excludes for brevity purposes, playing out the deployment decision of which 2Way-Meters are in-scope.

Figure 5.4-2 Alternative / Multiple Communication Paths – Options Example

The Path Option pseudo code for this graphic parsing is [1 or 2 or 3 or 4 or 5 or 6].

Payload Requirement Set Data Flow Ref Pseudo Code

The Requirement Table Parent rows’ “Data Flow Ref” column contains pseudo code, specific to that payload requirement set which is another way to document the communication paths and some of the deployment decision points. As an example, to sync up with the Reference Diagram snippet Figure 5.4-1, that contains the electric, gas, and water meters, the “CIS/Billing – Utility” to “2Way-Meter – electr or gas or water”, the Data Flow Ref pseudo code is

[(1Aa + 1B) or 1Ab] +

[1Ca or (1Cba + 1Cb) or (1Cba + 1Cc)] +

[1D or 1Dg or 1Dw]

Communication Path and Deployment Decisions Graphical Pseudo Code

Another approach to documenting the alternative communication paths and deployment decisions is the use of a combined graphic representation and pseudo code. For the “CIS/Billing – Utility” to “2Way-Meter –electr or gas or water”, the communication path decisions include:

- CIS/Billing to AMI Head-End (e.g. is the communications path with or without MDMS)

- AMI Head-End to DAP (across what networks and additional intermediary actors are being used, for which specific set of DAPs e.g. not all DAPs must use the same backhaul communications path to AMI Head-End)

The deployment decision for the “CIS/Billing – Utility” to “2Way-Meter – electr or gas or water”is

- DAP to 2Way-Meter (which meter: electr, gas, water, is driven by the deployment characteristics being studied)

These decisions are illustrated as:

Figure 5.4-3 Alternative / Multiple Communication Paths Decisions – “CIS/Billing – Utility to DAP” Example

Figure 5.4-4 Deployment Decision – Meter-2way Example

The resultant decisions pseudo code in this example is

with the resultant pseudo code being (using the decision index values):

[ (1a or 1b) + (2a or 2b or 2c) + (D1 or D2 or D3) ]

Mapping Across the Three Communication Path & Deployment Decision Methods

The relationship (mapping) across these three methods for documenting the communication path options and deployment decisions, provides the ability to translate from one method to another depending upon the readers or consumer of the SG Network TF Requirements preference.

Using the “CIS/Billing – Utility” to “2Way-Meter – electr or gas or water” example, the mapping across the three methods illustrate the intended interpretation of extracting the specific payloads as driven by the users specified communication path and deployment decisions.

| Graphic Parsing |  | Data Flow |  | Graphic Decisions |
| --- | --- | --- | --- | --- |
| [1 or 2 or 3 or 4 or 5 or 6] | = |  |  | [(1a or 1b) + (2a or 2b or 2c) +<D>] |
|  |  | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cc) or (1Cba + 1Cb)] + [1D or 1Dg or 1Dw] | = | [(1a or 1b) + (2a or 2b or 2c) + (D1 or D2 or D3)] |
| If the right hand side of the parent actor pairing was a specific actor and the same across all thread examples e.g. “Meter-2way-electr”, then all three methods would equate (via the pseudo code) to each other as shown below. |
| [1 or 2 or 3 or 4 or 5 or 6] | = | [(1Aa + 1B) or 1Ab] + [1Ca or (1Cba + 1Cc) or (1Cba + 1Cb)] + 1D | = | [(1a or 1b) + (2a or 2b or 2c) + D1 |
| And more specifically, if the communication path decision is (selecting on the Graphic Parsing option 5), the pseudo code results in the following equivalence |
| 5 | = | (1Aa + 1B) + (1Cba + 1Cc) + 1D | = | 1a + 2b + D1 |

Table 5.4-1 Communications Path & Deployment Decisions Pseudo Code Mapping – Meter-2way Example

These communication path and deployment decisions need to be made, and programmatically applied to the Requirement Table content (preferably as that capability in the Requirements Database), for the correct selection of the application requirements specific to the intended deployment being contemplated and/or studied.

The remainder of this section illustrates and describes in Graphic Decisions pseudo code, most of the communication path and deployment decision points as contained in Requirements Table 5.0.

Figure 5.4-5 Deployment Decision – Requirements Table 5.0

Figure 5.4-6 Communications Path Decision Set 1 – Requirements Table 5.0

Figure 5.4-7 Communications Path Decision Set 2 – Requirements Table 5.0

Figure 5.4-8 Communications Path Decision Set 3 – Requirements Table 5.0

Figure 5.4-9 Communications Path Decision Set 4 – Requirements Table 5.0

Figure 5.4-10 Communications Path Decision Set 5 – Requirements Table 5.0

Figure 5.4-11 Communications Path Decision Set 6 – Requirements Table 5.0

## Application Payloads

| Payload Name | Payload Type | Description | Application Payload-attributes (excludes comm packet fields), date-time-stamps assumed for all payloads | Security LICs - NISTIR 7628 - associated to Payloads | Non-Functional Application Payload C-I-A | Non-Functional Application Payload C-I-A Risk Values (and/or LIC) - Rational & Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Audit_Application_Event | Alert | Meter sends Meter event to Operations actor e.g. MDMS, occurs when a preconfigured criteria is met e.g.: a) failure or exception in an execution of an application or out of band/bounds condition; b) not able to service request or request timed out; c) system activity | Meter ID, event type/Code | 13 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive ack code associated to a specific meter may lead to an incorrect next workflow process execution that may lead to serious effect on safe reliable operation of the meter; A - not receiving this payload from a specific meter might lead to lead to an inappropriate action/operation being taken that may have a serious effect on safe reliable electric operation of the meter; |
| batt_pwr_notification | Alarm | Indication that network or end-point device is running solely on battery power | Device ID, status of mains power | 13, 20 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific device may lead to an unnecessary health check of the device; A - not receiving this payload from a specific device may lead to device becoming unavailable for it's intended role when battery power is drained, at which point lose of communication with device would eventually be detected. |
| bulk_Cust_Subset_Acct_Info_REP_data | resp-data | CIS/Billing - REP sends several large files (batches) of REP account information to the REP's ODW per day | Account ID, Premise ID, Premise address, billing address, Meter ID, payment history, current billing, general account information (programs enrolled in) - Utility meter customers | 7 | H-M-L | C - severe to catastrophic harm to customer or organization for access to/disclosure of payload data; I - inaccurate data (specific to more than one account), may lead to an incorrect next workflow process execution that may lead to serious lost of Customer trust and increased frustration with REP, and/or complaint filed with jurisdiction; A - not receiving this payload would create stale data for a batch of accounts and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_Acct_Info_Util_data | resp-data | CIS/Billing - Utility sends several large files (batches) of Utility account information to the Utility's ODW per day | Account ID, Premise ID, Premise address, billing address, Meter ID, payment history, current billing, general account information (programs enrolled in) - Utility meter customers | 7 | H-M-L | C - severe to catastrophic harm to customer or organization for access to/disclosure of payload data; I - inaccurate data (specific to more than one account), may lead to an incorrect next workflow process execution that may lead to serious lose of Customer trust and increased frustration with Utility, and/or complaint filed with jurisdiction; A - not receiving this payload would create stale data for a batch of accounts and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_Acct_Premise_Info_REP_data | resp-data | ODW - REP sends 1 large upload of REP customer account info per day to REP's web portal and optional Common Web Portal for access by the REP's customers | Account ID, Premise ID, Meter ID, Premise Address, billing address, payment history, current billing, general account information (programs enrolled in), energy/demand usage history, for REPs energy customers | `7/ 8 | H-M-L | C - severe to catastrophic harm to customer or organization for access to/disclosure of payload data; I - inaccurate data (specific to more than one account), may lead to serious lose of Customer trust and increased frustration with REP, and/or complaint filed with jurisdiction; A - not receiving this payload would create stale data for a batch of accounts and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_Acct_Premise_Info_Util_data | resp-data | ODW - Utility sends 1 large upload of Utility customer account info per day to Utility's web portal and optional Common Web Portal for access by the Utility's customers | Account ID, Premise ID, Meter ID, Premise Address, billing address, payment history, current billing, general account information (programs enrolled in), energy/demand usage history, for Utility's energy customers | `7/ 8 | H-M-L | C - severe to catastrophic harm to customer or organization for access to/disclosure of payload data; I - inaccurate data (specific to more than one account), may lead to serious lose of Customer trust and increased frustration with Utility, and/or complaint filed with jurisdiction; A - not receiving this payload would create stale data for a batch of accounts and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_meter_comm_Info_Util_data | resp-data | AMI Head-End sends several large files (batches) of meter information gathered from the Utility meters appropriate for storage/use in the ODW - Utility | Meter ID, meter read success stats | 7 | L-M-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate payload attributes (specific to more than one meter associated to a specific batch of meters), may lead to an unnecessary health check of the meter or telecomm network or associated applications or inaccurate reporting to jurisdictions; A - not receiving this payload would create stale data for a batch of meters and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_meter_Info_Util_data | resp-data | MDMS sends several large files (batches) of Utility meter information to the ODW - Utility | Meter ID, Current meter Readings, meter read history | 7 | M-M-L | C - serious harm to organization for not showing good stewardship (unauthorized access to/disclosure) of large amounts of meter payload data; I - inaccurate data (specific to more than one account), may lead to an incorrect next workflow process execution that may lead to serious lose of Customer trust and increased frustration with Utility, and/or complaint filed with jurisdiction; A - not receiving this payload would create stale data for a batch of accounts and may trigger an immediate retry or retry at next file transfer period |
| bulk_Cust_Subset_meter_outage_Info_Util_data | resp-data | OMS sends several large files (batches) per day of Utility Meter service outage information to ODW - Utility | Meter ID, outage information (reported outage, expected restore date/time, any assigned trouble ticket) | 7 | M-M-L | C - serious harm to organization for not showing good stewardship (unauthorized access to/disclosure) of large amounts of meter payload data; I - inaccurate payload attributes (specific to more than one meter), associated to a specific batch of meters may lead to an unnecessary health check of the meter or telecomm network or associated applications or inaccurate reporting to jurisdictions; A - not receiving this payload would create stale data for a batch of meters and may trigger an immediate retry or retry at next file transfer period |
| bulk_Mtr-read_cmd | Cmd | CIS/Billing - Utility requests several large files (batches) of Utility meter information from MDMS per day | group(cycle)ID, data-elements-groups, data-date | 7 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate command parameters associated to a batch of meters may lead to an incorrect next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that batch of meters; A - not receiving the response payload to this command would create missing data for a batch of meters and would trigger an immediate retry or retry at next file transfer period to satisfy next workflow processing steps (e.g. billing); |
| bulk_Mtr-read_resp-data | resp-data | MDMS sends several large files (batches) per day of Utility meter information to CIS/Billing - Utility | group(cycle)ID, data-elements-group ID (e.g. Meter ID, Register Readings, Interval Data, program-opt-outs, Voltage), data-date, | 7 | M-M-M | C - serious harm to organization for not showing good stewardship (unauthorized access to/disclosure) of large amounts of meter payload data, with minimal to harm to customer for unauthorized access to/disclosure of payload data; I - inaccurate positive command parameters associated to a batch of meters may lead to an incorrect next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that batch of meters; A - not receiving the payload would create missing data for a batch of meters and would trigger an immediate retry or retry at next file transfer period to satisfy next workflow processing steps (e.g. billing); |
| circuit_device_oper_cmd | Cmd | DMS or DAC sends an operate request to specific zone isolation or circuit restoring devices | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner (operating the wrong device and not completing the necessary zone isolation task) potentially causing the Utility significant financial impact or unsafe conditions to customers on impacted portions of the faulted circuit(s);. A - latent and un-reliable connections could cause the distribution grid to malfunction in a dangerous manner (operating the wrong device and not completing the necessary zone isolation task) potentially causing the Utility significant financial impact or unsafe conditions to customers on impacted portions of the faulted circuit(s);. |
| circuit_device_oper_cmd_ack | Ack | specific zone isolation or circuit restoring device sends command receipt/operation acknowledgement to DMS or DAC | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the inappropriate workflow next step execution, distribution grid to malfunction in a dangerous manner (operating the wrong device and not completing the necessary zone isolation task) potentially causing the Utility significant financial impact (if follow-up device status not implemented) or unsafe conditions to customers on impacted portions of the faulted circuit(s); A - latent and un-reliable connections could cause the distribution grid to malfunction in a dangerous manner (operating the wrong device and not completing the necessary zone isolation task) potentially causing the Utility financial impact or unsafe conditions to customers on impacted portions of the faulted circuit;. |
| circuit_device_self-init_status_resp-data | resp-data | specific zone isolation or circuit restoring device sends self initiated device status to DMS or DAC | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause incorrect workflow next task execution that may lead to the distribution grid malfunction in a dangerous manner potentially causing significant impact (if follow-up or routine device status requests not implemented) to the Utility and the Customer financials. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| circuit_device_status_cmd | Cmd | DMS or DAC sends device status request to specific zone isolation or circuit restoring devices | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause either the correct device to attempt to perform an inappropriate action or the wrong device to perform an action all of which may lead to unsafe or malfunction operation of the distribution grid that may have severe to catastrophic harm (especially if in-scale) to Utility and/or Customer; A - latent and un-reliable connections may lead insufficient data for application to determine zone-isolation/circuit-reconfig actions (especially if in-scale), which might lead to significantly more customers being without power than necessary. |
| circuit_device_status_resp-data | resp-data | specific zone isolation or circuit restoring devices send device status to DMS or DAC | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing significant impact (especially if follow-up device status checks not implemented or if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections may lead insufficient data for application to determine zone-isolation/circuit-reconfig actions, which might lead to more customers being without power than necessary. |
| circuit-brk_device_status_cmd | Cmd | DAC sends device status request to circuit breaker | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause either the correct device to attempt to perform an inappropriate action or the wrong device to perform an action all of which may lead to unsafe or malfunction operation of the distribution grid that may have severe to catastrophic harm to the Utility and/or Customer; A - latent and un-reliable connections may lead insufficient data for application to determine zone-isolation/circuit-reconfig actions, which might lead to more customers being without power than necessary. |
| circuit-brk_status_resp-data | resp-data | circuit breaker sends device status to DAC | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing significant impact (especially if follow-up device status checks for missing response data not implemented) to the Utility and the Customer financials A - latent and un-reliable connections may lead insufficient data for application to determine zone-isolation/circuit-reconfig actions, which might lead to more customers being without power than necessary. |
| Configuration_Event | Alarm | Meter sends message meter indicating configuration has changed for that device e.g. out-of-state condition with configuration; get / set config, config errors | Meter ID, acknowledgement code | 13 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive alarm code associated to a specific meter may lead to an incorrect next workflow process execution that may lead to severe or catastrophic impact on safe reliable economic operation of the meter (if in-scale); A - not receiving this payload from a specific meter might lead to an inappropriate action/operation being taken that may have a severe or catastrophic impact on safe reliable economic operation of the meter (if in-scale); |
| Cust_Acct_Info_cmd | Cmd | Customer (after a separate authentication to their energy providers web portal), sends a request for Customer's account information | Account ID, query type | 16 | M-M-L | C - minimal to serious harm to customer or organization (if in-scale), for access to/disclosure of Account ID and query type; I - inaccurate account ID and query type could lead to serious impact (if in-scale) to incorrect customer-to-accountID association e.g. wrong results sent to the wrong customer A - not receiving this payload could lead to customer frustration and/or complaint being filed with jurisdiction |
| CPP_pricing-data_ack | ack | HAN device participating in the CPP event sends message to LMS or DSM for either Utility of REP, acknowledging receipt and processing of the CPP command | HAN device ID, acknowledgement code | 13, 15/16 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - minimal harm to customer or organization if a false acknowledgement from the wrong HAN device is sent/received, provided not in-scale. A - Receipt of these messages need to completed in a reasonable time. |
| CPP_pricing-data_brdcst | cmd | LMS or DSM for either Utility of REP sends CPP event command to all CPP enrolled HAN devices | HAN device broadcast group ID, CPP price data, CPP effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| CPP_pricing-data_cmd | cmd | LMS or DSM for either Utility of REP sends CPP event command to specific CPP enrolled HAN device | HAN device ID, CPP effective time period, CPP price data | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| CPP_pricing-data_mltcst | cmd | LMS or DSM for either Utility of REP sends CPP event command to specific groups of CPP enrolled HAN devices | HAN device multicast group ID, CPP price data, CPP effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| Cust_Acct_Info_resp-data | resp-data | Energy providers Web Portal sends requested Customer's account information to Customer's web interface (after Customer authentication/authorization) | Customer's: Account ID, Premise ID, Meter ID, Premise Address, billing address, payment history, current billing, general account information (programs enrolled in), energy/demand usage history | 16 | H-M-L | C - limited harm to customer (unless name included and associated to account ID) and severe to catastrophic harm to organization especially in-scale, for access to/disclosure of payload data; I - inaccurate account ID and/or query type could lead to a customers account information sent to the wrong party or correct customer taking inappropriate actions based on the response data; A - not receiving this payload could lead to customer frustration and/or complaint filed with jurisdiction |
| DAP_firmware_update_cmd | cmd | AMI Head-End or Field Tool sends command to initiate a firmware update on a DAP. DAP is not a electric grid critical infrastructure component except if it the DAP provides communications to distribution equipment. This payload is not used primarily for disturbance analysis. | device ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | L:-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - serious to severe harm (if used for comm with crticial infrastructure or in-scale) if inaccurate Device ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - failed firmware updates commands are assumed to be retried if failed without consequence. |
| DAP_firmware_update_confirmation | resp-data | DAP sends confirmation of completion of DAP firmware upgrade to AMI Head-End or Field Tool. DAP is not a electric grid critical infrastructure component except if it the DAP provides communications to distribution equipment. This payload is not used primarily for disturbance analysis. | device ID, success or fail notification, firmware revision information | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - moderate harm (if in-scale) if inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - moderate harm (if in-scale) if failed firmware updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| DAP_program_update_cmd | cmd | AMI Head-End or Field Tool sends command to initiate a Program/Configuration command to a DAP. DAP is not a electric grid critical infrastructure component except if it the DAP provides communications to distribution equipment. This payload is not used primarily for disturbance analysis. | device group ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with device ID, firmware version number and cut over information. I - serious to severe operational reliable econmic harm (if DAP comm to critical infrastructure or in-scale) if inaccurate Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - failed configuration/program update commands are assumed to be retried if failed without consequence. |
| DAP_program_update_confirmation | resp-data | DAP sends response that a DAP configuration/program command has been completed to AMI Head-End or Field Tool. DAP is not a electric grid critical infrastructure component except if it the DAP provides communications to distribution equipment. This payload is not used primarily for disturbance analysis. | device ID, acknowledgement code | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data;ID, acknowledgement code and cut over information. I - moderate harm if inaccurate device ID , success vs fail status and configuration/program version could lead a utility to believe a system is up to date when incorrect. A - moderate harm if failed configuration/programming updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| distr_cust_storage_charge-rate_cmd | cmd | DAC sends specific charge-rate request to Distr Cust Storage device | device ID, command code, charging-rate-value | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID charging-rate-value and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing serious harm to Utility (if in -scale) and minimum to serious harm to Customer; A - latent and un-reliable connections could cause the operation requested to seriously harm the electric network |
| distr_cust_storage_charge-rate_cmd_ack | ack | Distr Cust Storage device sends charge-rate command receipt/command initiation acknowledgement to DAC | device ID, acknowledgement code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to be operated in an unsafe/unstable manner potentially causing serious impact (if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impacts if the operator of the network does not understand the state of the electric grid. |
| distr_cust_storage_discharge_cmd | cmd | DAC sends specific discharge request to Distr Cust Storage device | device ID, command code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID charging-rate-value and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing serious harm to utility (if in -scale) and minimum to serious harm to Customer; A - latent and un-reliable connections could cause the operation requested to seriously harm (if in-scale) the electric network |
| distr_cust_storage_discharge_cmd_ack | ack | Distr Cust Storage device sends discharge command receipt/command initiation acknowledgement to DAC | device ID, acknowledgement code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to be operated in an unsafe/unstable manner potentially causing serious impact (if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impacts (if in-scale) if the operator of the network does not understand the state of the electric grid. |
| distr_cust_storage_in-island-mode_alarm | alarm | Distr Cust Storage device sends in-island-mode and discharging alarm to DAC and is relayed to Operations actors | device ID, alarm code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid applications to take inappropriate workflow next task executions if the current state of zoned devices not validated, which may lead to unsafe/unstable grid operations, potentially causing serious impact (if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impact (if in-scale) if the operator of the network does not understand the state of the electric grid. |
| distr_cust_storage_out-of-island-mode_alert | alert | Distr Cust Storage device sends out-of-island-mode and stop discharging alert to DAC and is relayed to Operations actors | device ID, alert code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid applications to take inappropriate workflow next task executions if the current state of zoned devices not validated, which may lead to unsafe/unstable grid operations, potentially causing serious impact (if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impact if the operator of the network does not understand the state of the electric grid. |
| distr_cust_storage_status_cmd | cmd | DAC sends device status request to specific Distr Cust Storage device | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing severe impact (if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impact if the operator of the network does not understand the state of the electric grid. |
| distr_cust_storage_status_resp-data | resp-data | Distr Cust Storage device sends device status data to DAC and is relayed to Operations actors | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing severe impact (if in scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause serious impact if the operator of the network does not understand the state of the electric grid. |
| ESI_firmware_update_cmd | cmd | Field Tool sends command to an ESI in the Meter to update the firmware on the device. ESI is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, firmware version number, firmware update | 13, 20, 21 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cutover information. I - severe operational reliable economic harm (if in-scale) if inaccurate Device ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - failed firmware updates commands are assumed to be retried if failed without consequence. |
| ESI_firmware_update_confirmation | resp-data | ESI - in Meter sends response indicating completion of a ESI firmware update to Firld Tool. ESI is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, acknowledgement code | 13, 20, 21 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update confirmation, with device ID, firmware version number and cutover information. I - moderate harm if inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - moderate harm if failed firmware updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| FAN-GtWay_firmware_update_cmd | cmd | Distr SCADA FEP or Field Tool sends command to initiate a firmware update on a FAN Gateway. FAN Gateway is not a electric grid critical infrastructure component except if it the FAN Gateway provides communications to any critcal infrastructure grid equipment. This payload is not used primarily for disturbance analysis. | device ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | M-H-L | C - moderate to serious impact on Utility's ability to monitor and operate the electric Distribution grid feeder devices, if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cutover information. I - serious to severe harm on Utility's ability to monitor and operate the electric Distribution grid feeder devices (if used for comm with especially crticial infrastructure or in-scale) if inaccurate Device ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - failed firmware updates commands are assumed to be retried if failed without serious consequence. |
| FAN-GtWay_firmware_update_confirmation | resp-data | FAN Gateway sends confirmation of completion of FAN Gateway firmware upgrade to Distr SCADA FEP or Field Tool. FAN Gateway is not a electric grid critical infrastructure component except if it the FAN Gateway provides communications to critical infrastructure grid equipment. This payload is not used primarily for disturbance analysis. | device ID, success or fail notification, firmware revision information | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if failed firmware updates confirmations are assumed to be retried if failed without consequence, however confirmation is expected to be guaranteed |
| FAN-GtWay_program_update_cmd | cmd | Distr SCADA FEP or Field Tool sends command to initiate a Program/Configuration command to a FAN Gateway. FAN Gateway is not a electric grid critical infrastructure component except if it the FAN Gateway provides communications to critical infrastructure grid equipment. This payload is not used primarily for disturbance analysis. | device group ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | M-H-L | C - up to serious impact on Utility's ability to monitor and operate the electric Distribution grid feeder devices, if an adversary is able to ascertain the program update command, with device ID, program version number and cutover information. I - serious to severe harm on Utility's ability to monitor and operate the electric Distribution grid feeder devices (if used for comm with especially crticial infrastructure or in-scale) if inaccurate Device ID, program could lead to a device loading incorrect program, cutover time could lead to a device updating before the system is ready. A - failed program updates commands are assumed to be retried if failed without serious consequence. |
| FAN-GtWay_program_update_confirmation | resp-data | FAN Gateway sends response that a FAN Gateway configuration/program command has been completed to Distr SCADA FEP or Field Tool. FAN Gateway is not a electric grid critical infrastructure component except if it the FAN Gateway provides communications to critical infrastructure grid equipment. This payload is not used primarily for disturbance analysis. | device ID, acknowledgement code | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - up to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if inaccurate device ID , success vs fail status and program version could lead a utility to believe a system is up to date when incorrect. A - up to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if failed program updates confirmations are assumed to be retried if failed without consequence, however confirmation is expected to be guaranteed |
| Fault_Error_Alarm_Event | alarm | Meter sends message to Operations e.g. MDMS, indicating an alarm condition has occurred e.g. out of predefined state or passed threshold conditions; System failure (e.g. Register), measurement failure, Service switch, system restart counts (outages), low battery, buggy software, firmware update failure, Communication errors, System memory full, system memory fail | Meter ID, alarm code | 13 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive alarm code associated to a specific meter may lead to an incorrect next workflow process execution that may lead to serious effect on safe reliable operation of the meter; A - not receiving this payload from a specific meter might lead to lead to an inappropriate action/operation being taken that may have a serious effect on safe reliable electric operation of the meter; |
| fault_lock_out_alarm | alarm | fault clearing device sends lock-out alarm to Operations actors | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code may cause Utility not recognizing the correct operational state of the distribution grid and if failing to perform a follow-up device state request, may lead to incorrect workflow next task execution, which may lead to severe harm to safe reliable economic (if other circuit device status requests are not implemented and if in-scale) grid operations and harm to Customer; A - latent and un-reliable connections could cause the operator of the electrical grid to perform unnecessary health checks of the devices and the telecomm network, and lead to lose of trust in distribution applications to function properly, leading to severe harm (if other circuit device status requests are not implemented and if in-scale) to organization and customer. |
| Fdr-dev-cntl_firmware_update_cmd | cmd | Distr SCADA FEP or Field Tool sends command to initiate a firmware update on a feeder device controller. Feeder device controller typically is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | M-H-L | C - moderate to serious impact on Utility's ability to monitor and operate the electric Distribution grid feeder devices, if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cutover information. I - serious to severe harm on Utility's ability to monitor and operate the electric Distribution grid feeder devices (especially for any crticial infrastructure or in-scale) if inaccurate Device ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - failed firmware updates commands are assumed to be retried if failed without serious consequence. |
| Fdr-dev-cntl_firmware_update_confirmation | resp-data | Feeder Device controller sends confirmation of completion of feeder device controller firmware upgrade to Distr SCADA FEP or Field Tool. Feeder device controller typically is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, success or fail notification, firmware revision information | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if failed firmware updates confirmations are assumed to be retried if failed without consequence, however confirmation is expected to be guaranteed |
| Fdr-dev-cntl_program_update_cmd | cmd | Distr SCADA FEP or Field Tool sends command to initiate a Program/Configuration command to a feeder device controller. Feeder device controller typically is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device group ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13/14, 20 | M-H-L | C - moderate to serious impact on Utility's ability to monitor and operate the electric Distribution grid feeder devices, if an adversary is able to ascertain the program update command, with device ID, program version number and cutover information. I - serious to severe harm on Utility's ability to monitor and operate the electric Distribution grid feeder devices (especially for any crticial infrastructure or in-scale) if inaccurate Device ID, program could lead to a device loading incorrect program, cutover time could lead to a device updating before the system is ready. A - failed program updates commands are assumed to be retried if failed without serious consequence. |
| Fdr-dev-cntl_program_update_confirmation | resp-data | Feeder device controller sends response that a feeder device controller configuration/program command has been completed to Distr SCADA FEP or Field Tool. Feeder device controller typically is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, acknowledgement code | 13/14, 20 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if inaccurate device ID , success vs fail status and program version could lead a utility to believe a system is up to date when incorrect. A - moderate to serious harm to ability of Utility's Distribution electric grid feeder device monitoring & operations (if in-scale) if failed program updates confirmations are assumed to be retried if failed without consequence, however confirmation is expected to be guaranteed |
| FeederCBC_alarm | alarm | feeder Capacitor Bank Controller has detected and sends an alarm notification | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous manner potentially causing severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if in-scale) to the Utility and the Customer financials A - latent and un-reliable connections could cause the operation requested to seriously harm (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if in-scale) the electric network |
| FeederCBC_close_ack | ack | feeder Capacitor Bank Controller has performed and sends a close operation acknowledgement | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a seriously (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and followup device status request not implemented and if in-scale) dangerous manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and seriously harm the electric network (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if in-scale). |
| FeederCBC_close_cmd | cmd | Command to close feeder Capacitor Bank | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a severe (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if in-scale) and dangerous manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operator of the network to not be able to operate Feeder Capacitor bank controllers in a timely manner. Prior to adding this functionality, crews were dispatched to operate these commands |
| FeederCBC_deviation_alert | alert | feeder Capacitor Bank Controller has detected and sends a measured value has gone out of the tolerance band alert | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a severe (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) and dangerous manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operation requested to severely harm (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) the electric network |
| FeederCBC_new_config_ack | ack | feeder Capacitor Bank Controller has received, processed and sends a new configuration acknowledgement | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous manner potentially causing serious to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) the Utility and the Customer financial impact. A - latent and un-reliable connections could cause serious impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) if the operator of the network does not understand the state of the electric grid. |
| FeederCBC_new_config_cmd | cmd | Command to perform a feeder Capacitor Bank Controller new configuration | device ID, configuration command, configuration information | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID configuration information and configuration command could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operation requested to severely harm (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) the electric network |
| FeederCBC_open_ack | ack | feeder Capacitor Bank Controller has performed and sends an open operation acknowledgement | device ID, acknowledgement code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid causing serious up to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) . |
| FeederCBC_open_cmd | cmd | Command to open feeder Capacitor Bank | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network causing serious up to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) |
| FeederCBC_Operate_failure | alarm | Message to indicate device failure | device ID, failure code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and failure code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact. (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network causing serious up to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) . |
| FeederCBC_sensor_data_cmd | cmd | Query for sensor data | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact.(if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| FeederCBC_sensor_data_resp-data | resp-data | sensor data response from feeder Capacitor Bank Controller | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact.(if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| FeederCBC_status_change_alert | alert | feeder Capacitor Bank Controller detects and sends device state change alert | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact.(if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network causing serious up to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) . |
| FeederCBC_status_cmd | cmd | Command to feeder Capacitor Bank Controller to query device status | device ID, query code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and query code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact.(if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| FeederCBC_status_resp-data | resp-data | feeder Capacitor Bank Controller response data to device status query | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact.(if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| FeederFault_Detector_alarm | alarm | feeder fault detection device senses a fault and sends a fault alarm | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to be operated in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause follow-up grid operations to potentially severely harm the electric grid, (if not recognized and coupled with other multiple sensor value adnomalies and if in-scale) |
| FeederFault_Detector_deviation_alert | alert | feeder fault detection device senses and sends a measured value has gone out of the tolerance band alert | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to be operated in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with other multiple sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause follow-up grid operations to potentially severely harm the electric grid, (if not recognized and coupled with other multiple sensor value adnomalies and if in-scale) |
| FeederFault_Detector_sensor_data_cmd | cmd | Query for feeder fault detector device sensor data | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederFault_Detector_sensor_data_resp-data | resp-data | sensor data response from feeder fault detector | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederFault_Detector_status_change_alert | alert | feeder Fault Detector detects and sends device state change alert | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to be operated in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with other multiple sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause follow-up grid operations to potentially severely harm the electric grid, (if not recognized and coupled with other multiple sensor value adnomalies and if in-scale) |
| FeederFault_Detector_status_cmd | cmd | command to check status of feeder Fault Detector | device ID, query operation | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and query operation could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederFault_Detector_status_resp-data | resp-data | feeder Fault Detector response data to device status query | device ID, condition, history if available | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID condition and history could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederRecloser_alarm | alarm | Alarm message to SCADA system | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operation requested to harm the electric network and may lead to severe incorrect electric grid operations. |
| FeederRecloser_deviation_alert | alert | Alert message to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operation requested to harm the electric network and may lead to severe incorrect electric grid operations. |
| FeederRecloser_new_config_ack | ack | Acknowledgement of new configuration | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to severe incorrect electric grid operations |
| FeederRecloser_new_config_cmd | cmd | Command to change configuration | device ID, configuration command | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and configuration command could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if situation not recognized quickly). A - latent and un-reliable connections could cause the operation requested to harm the electric network and lead to severe missed operations (if not recognized quickly) |
| FeederRecloser_Operate_failure | alarm | Message to indicate device failure | device ID, failure code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and failure code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operation requested to harm the electric network and may lead to severe incorrect electric grid operations. |
| FeederRecloser_sensor_data_cmd | cmd | Query to sensor data | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if situation not recognized quickly) A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized quickly) |
| FeederRecloser_sensor_data_resp-data | resp-data | Response from recloser | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly) A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized quickly) |
| FeederRecloser_status_change_alert | alert | Alert message to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to severe incorrect electric grid operations. |
| FeederRecloser_status_cmd | cmd | Command to recloser to query status | device ID, query code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and query code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly) A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized) |
| FeederRecloser_status_resp-data | resp-data | response to recloser query status | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly) A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized) |
| FeederSensor_alarm | alarm | Alarm message to SCADA system | device ID, alarm code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact (if coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operation requested to seriously harm the electric network (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_deviation_alert | alert | feeder Sensor has detected and sends a measured value has gone out of the tolerance band alert | device ID, alert code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact.(if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid.and lead to serious operations (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_new_config_ack | ack | Acknowledgement of new configuration | device ID, acknowledgement code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_new_config_cmd | cmd | Command to change configuration | device ID, command code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_sensor_data_cmd | cmd | Command to query sensor data | device ID, sensor data | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious missed operations (if not recognized and coupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_sensor_data_resp-data | resp-data | Response to Sensor query | device ID, response data | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and lead to serious incorrect operation of the grid (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_status_change_alert | alert | Alert to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer severe financial impact (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid of the grid and lead to severe incorrect operation (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_status_cmd | cmd | Command to sensor for status | device ID, command code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to incorrect operation of the grid (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSensor_status_resp-data | resp-data | Response to sensor status request | device ID, sensor status | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and sensor status could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect operation of the grid (if not recognized andcoupled with multiple other CBC, Regulator sensor value adnomalies and if in-scale). |
| FeederSwitch_alarm | alarm | Alarm message to SCADA system | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operation requested to severely harm the electric network |
| FeederSwitch_close_ack | ack | Acknowledgment of switch close | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement status could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid. |
| FeederSwitch_close_cmd | cmd | Command to close feeder switch | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly). A - latent and un-reliable connections could cause the operation requested to severely harm the electric network (if not recognized quickly) |
| FeederSwitch_deviation_alert | alert | Alert to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrectly operate the grid in a dangerous/severe manner. |
| FeederSwitch_new_config_ack | ack | feeder Switch Controller has received, processed and sends a new configuration acknowledgement | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous manner potentially causing serious to severe impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) the Utility and the Customer financial impact. A - latent and un-reliable connections could cause serious impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) if the operator of the network does not understand the state of the electric grid. |
| FeederSwitch_new_config_cmd | cmd | Command to perform a feeder Switch Controller new configuration | device ID, configuration command, configuration information | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID configuration information and configuration command could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale). A - latent and un-reliable connections could cause the operation requested to severely harm (if coupled with multiple other circuit regulator & voltage sensor value adnomalies and if follow-up circuit device stats request not implemented and if in-scale) the electric network |
| FeederSwitch_open_ack | ack | Confirmation of switch open | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrectly operate the grid in a dagerous/serious manner |
| FeederSwitch_open_cmd | cmd | Command to open feeder switch | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly). A - latent and un-reliable connections could cause the operation requested to severely harm the electric network (if not recognized quickly) |
| FeederSwitch_Operate_failure | alarm | Alarm message to SCADA system | device ID, alarm code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized quickly). A - latent and un-reliable connections could cause the operation requested to severely harm the electric network (if not recognized quickly) |
| FeederSwitch_sensor_data_cmd | cmd | Query to switch for data | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a severe dangerous manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederSwitch_sensor_data_resp-data | resp-data | Response for switch sensor | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and may lead to serious incorrect electric grid operations. |
| FeederSwitch_status_change_alert | alert | Alert to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect dangerous/severe operation of the grid |
| FeederSwitch_status_cmd | cmd | Query to feeder switch for status | device ID, command code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect dangerous/setious operation of the grid |
| FeederSwitch_status_resp-data | resp-data | Switch status response | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect dangerous/serious peration of the grid |
| FeederVR_alarm | alarm | Alarm message to SCADA system | device ID, alarm code | 2, 4 | L-M-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect serious operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_deviation_alert | alert | Alert to SCADA system | device ID, alert code | 2, 4 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect serious operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_new_config_ack | ack | Acknowledgement of new configuration | device ID, acknowledgement code | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect serious operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_new_config_cmd | cmd | Command for new VR config | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_Operate_failure | alarm | Alert to SCADA system | device ID, alarm code | 2, 4 | L-M-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alarm code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_sensor_data_cmd | cmd | Command to query sensor data | device ID, command code | 2, 4 | L-L-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and serious incorrect operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_sensor_data_resp-data | resp-data | response from sensor | device ID, response data | 2, 4 | L-L-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous but minimal manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and serious incorrect operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_status_change_alert | alert | Alert to SCADA system | device ID, alert code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and alert code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operation requested to severely harm the electric network and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_status_cmd | cmd | Query VR status | device ID, command code | 2, 4 | L-L-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous manner potentially causing the Utility and the Customer financial impact. A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect serious operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_status_resp-data | resp-data | VR Status response | device ID, response data | 2, 4 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and response data could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect serious operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_step_down_ack | ack | Acknowledgement step down | device ID, acknowledgement code | 2, 4 | L-M-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_step_down_cmd | cmd | Command to VR to step down | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_step_up_ack | ack | Acknowledgement of step up | device ID, acknowledgement code | 2, 4 | L-M-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and acknowledgement code could cause the distribution grid to malfunction in a dangerous/serious manner potentially causing the Utility and the Customer serious financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operator of the network to not understand the state of the electric grid and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| FeederVR_step_up_cmd | cmd | Command to VR to step up | device ID, command code | 2, 4 | L-H-H | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - incorrect device ID and command code could cause the distribution grid to malfunction in a dangerous/severe manner potentially causing the Utility and the Customer severe financial impact (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). A - latent and un-reliable connections could cause the operation requested to harm the electric network and incorrect severe operation of the grid (if not recognized and coupled with multiple other CBC, voltage sensor value adnomalies and if in-scale). |
| han_dev_join_ack | ack | HAN devices send to CIS / Billing acknowledgement that HAN device has successfully processed the join request | device ID, mac address, acknowledgement code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and acknowledgement code will cause the Demand Response system to not have correct information about where load control devices are installed A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device joined the network |
| han_dev_join_cmd | cmd | CIS / Billing sends command to initiate the join command to HAN devices | device ID, mac address, security material, operation timeout value, command code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and command code will cause the Demand Response system to not have correct information about where load control devices are installed A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device joined the network |
| han_dev_join_cmd_err | cmd-err | HAN device sends HAN device join request error to CIS / Billing and NMS | device ID, mac_address, error code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and error code will cause the Demand Response system to not properly troubleshoot communication problems A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device joined the network |
| han_dev_un_join_ack | ack | HAN device sends to CIS / Billing acknowledgement that HAN device has successfully processed the un_joined command | device ID, mac address, acknowledgement code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and acknowledgement code will cause the Demand Response system to not have correct information about where load control devices are un-installed A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device un-joined the network |
| han_dev_un_join_cmd | cmd | CIS / Billing sends command to initiate the un-join command to HAN devices | device ID, mac address, command code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and command code will cause the Demand Response system to not have correct information about where load control devices are un-installed A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device un-joined the network |
| han_dev_un-join_cmd_err | cmd-err | HAN device sends HAN device join request error to CIS / Billing and NMS | device ID, mac_address, error code | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate device ID, mac address and error code will cause the Demand Response system to not properly troubleshoot communication problems A - not receiving the response payload to this command would cause the customer and the energy service provider to not have timely feedback about whether a device joined the network |
| Load_mgm_opt_out | cmd | HAN device sends message to LMS or DSM that Customer declined participation in load control event. | device ID(s), mac address(s), event ID(s), | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - an incorrect device id/mac address and opt-out event id may cause the utility to not understand the correct customer opted out of the load control event and possibly penalize the wrong customer for opt-in out too many times. A - Receipt of these messages need to completed in a reasonable time but are not critical. |
| Load_mgm_req_ack | ack | HAN device sends message to LMS or DSM acknowledging customer HAN deive received the load management event. | device ID, mac address, acknowledgement code, event ID, estimation of load reduction | 13, 15/16 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - Caller of the load management event needs to understand the message is properly received by the intended devices. A - Receipt of these messages need to completed in a reasonable time but are not critical. |
| Load_mgm_reqst | cmd | LMS or DSM sends a load management event message to HAN device | device ID, mac_address, event ID, event time and duration, randomization value for start and stop, load adjustment percentage, maximum duty cycle, criticality level, | 13, 15/16 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |
| Load_mgm_reqst_brdcst | cmd | LMS or DSM sends a broadcasted load management event to customers HAN device of a planned event. | broadcast ID, event ID, event time and duration, randomization value for start and stop, load adjustment percentage, maximum duty cycle, criticality level, | 13, 15/16 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |
| Load_mgm_reqst_mltcst | cmd | LMS or DSM sends a multicast load management event notifying specific group of customers' HAN devices of a planned event. | device group ID, event ID, event time and duration, randomization value for start and stop, load adjustment percentage, maximum duty cycle, criticality level, | 13, 15/16 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |
| meter_capped_kwh_mode_cancel_cmd | cmd | LMS sends cancel meter-capped-kwh-mode command to specific 2-Way Meters - Electr. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, command code | 13/14 | M-M-M | C - minimal harm to customer or organization reputation for allowing access to/disclosure of payload data as payload is tied to Meter ID not customer account ID or name; I - inaccurate command parameters associated to a meter may lead to an incorrect command being applied to the correct meter or command being sent to the wrong meter with most harm being going back to normal or a service switch operate, when should stay in capped kwh mode, which may lead to minimal harm to customer or minimum to serious trust impact to utility (if in -scale); A - not receiving the command would produce capped kwh mode and customer power disconnects after full power is restored, leading to customer frustration and probable complaint filed with jurisdiction; |
| meter_capped_kwh_mode_cancel_cmd_ack | ack | 2-Way Meter - Electr sends cancel meter-capped-kwh-mode command receipt/operate acknowledgement to LMS & MDMS. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, acknowledgement code | 13/14 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data as payload is tied to Meter ID not customer account ID or name; I - These messages need to be properly attributed to the Meter that sent them, none to minimal harm to electric grid; A - minimal harm to comer or organization for failure of receipt of this payload, no harm to electrical grid other than accelerated discharge of distributed customer storage device. |
| meter_capped_kwh_mode_cmd | cmd | LMS sends meter-capped-kwh-mode command to specific 2-Way Meters - Electr. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, command code | 13/14 | M-H-M | C - minimal harm to customer or organization reputation for allowing access to/disclosure of payload data as payload is tied to Meter ID not customer account ID or name; I - inaccurate command parameters associated to a meter may lead to an incorrect command being applied to the correct meter or command being sent to the wrong meter resulting in meter staying in normal mode or a service switch operation, rather than going into capped kwh mode, which may lead to minimum to serious harm to life support customers and severe impact to utility if in -scale; A - not receiving the command would produce accelerated discharge of distributed customer storage device; |
| meter_capped_kwh_mode_cmd_ack | ack | 2-Way Meter - Electr sends meter-capped-kwh-mode command receipt/operate acknowledgement to LMS & MDMS. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, acknowledgement code | 13/14 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data as payload is tied to Meter ID not customer account ID or name; I - These messages need to be properly attributed to the Meter that sent them, none to minimal harm to electric grid; A - minimal harm to customer or organization for failure of receipt of this payload, no harm to electrical grid other than accelerated discharge of distributed customer storage device. |
| meter_in_capped_kwh_mode_alert | alert | 2-Way Meter - Electr sends meter-capped-kwh-mode alert to IHD, Cust EMS, MDMS. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, alert code, alert text | 13/14 | L-M-M | C - none to minimal harm to customer or organization reputation for allowing access to/disclosure of payload data as payload associated to Meter ID not customer account ID or name; I - inaccurate payload attributes associated to Meter may lead to unnecessary actions taken by customer to reduce power consumption, which may result in customer complaints to jurisdictions (if in-scale) A - not receiving this payload by the customer IHD or Customer EMS may lead to accelerated distributed customer storage device and/or customer's service switch open operation (lose of power) |
| meter_out_of_capped_kwh_mode_alert | alert | 2-Way Meter - Electr sends meter-out-of-capped-kwh-mode alert to IHD, Cust EMS, MDMS. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. | Meter ID, alert code, alert text | 13/14 | L-H-M | C - none to minimal harm to customer or organization reputation for allowing access to/disclosure of payload data as payload associated to Meter ID not customer account ID or name; I - inaccurate payload attributes associated to Meter may lead to customer not realizing a return to normal operations and normal power consumption patterns; A - not receiving this payload by the customer IHD or Customer EMS may lead to prolonged Customer's self initiated reduced power consumption actions, which may lead to customer frustration and may lead to complaint filed with jurisdiction |
| metrology_firmware_update_broadcast_cmd | cmd | AMI Head-End sends command to initiate the metrology firmware update on a large body of meters. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | timeout, firmware version number , cut over time or cut over parameters | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| metrology_firmware_update_cmd | cmd | AMI Head-End sends command to initiate a firmware update on a single meter. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, timeout, firmware version number , cut over time or cut over parameters | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| metrology_firmware_update_confirmation | resp-data | Meter sends confirmation of completion of firmware upgrade to MDMS and/or Field Tool. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, success or fail notification, firmware revision information | 13, 20 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update confirmation, with device ID, firmware version number and cut over information. I - Inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - Failed firmware updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| metrology_firmware_update_multicast_cmd | cmd | AMI Head-End sends command to initiate a firmware update to a defined group of meters. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device group ID, timeout, firmware version number , cut over time or cut over parameters | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with Group device ID, firmware version number and cut over information. I - Inaccurate Device group ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| metrology_program_update_broadcast_cmd | cmd | AMI Head-End sends command to initiate a program update on a large body of meters. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | timeout, program version number, cut over time or cut over parameters, program update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with Group device ID, and cut over information. I - Inaccurate Group Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - Failed configuration/program update commands are assumed to be retried if failed without consequence. |
| metrology_program_update_cmd | cmd | AMI Head-End sends command to initiate a meter program update on a single meter. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, timeout, program version number, cut over time or cut over parameters, program update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with device ID, firmware version number and cut over information. I - Inaccurate Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - Failed configuration/program update commands are assumed to be retried if failed without consequence. |
| metrology_program_update_confirmation | resp-data | Meter sends confirmation of completion of program change to MDMS and/or Field Tool. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, success or fail notification, program revision information | 13, 20 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program confirmation, with device ID, acknowledgement code and cut over information. I - Inaccurate device ID , success vs fail status and configuration/program version could lead a utility to believe a system is up to date when incorrect. A - Failed configuration/programming updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| metrology_program_update_multicast_cmd | cmd | AMI Head-End sends command to initiate a program change to a defined group of meters. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device group ID, timeout, program version information, cut over time or cut over parameters, program update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with Group device ID, and cut over information. I - Inaccurate Group Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - Failed configuration/program update commands are assumed to be retried if failed without consequence. |
| Mtr-read_data_resp-data | resp-data | 2-Way Meters - Water send meter read data to AMI Head-End. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, reading period, reading type, reading data | 13 | M-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate payload data associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter, or customer taking incorrect action that if happens in-scale may lead to serious impact to customers or the organization; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again, may wait for next time periods send of meter read data and then processing for multiple time periods; |
| Mtr-read_multi-interval-data_cmd | cmd | Operations e.g. MDMS actor sends command requesting a specific interval of meter consumption information for a specific period from 2-Way Meter (Electr or Gas). Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, period of time to be reported, reading type | 13 | M-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account, but made lead to serious impact to Utility if in-scale I - inaccurate Meter ID, reading period and reading type can lead to billing errors and customer complaints leading to serious harm to utility (if in-scale) A - not receiving the payload would create missing meter data and would trigger an immediate retry or retry at next file transfer period to satisfy next workflow processing steps (e.g. billing); |
| Mtr-read_multi-interval-data_resp-data | resp-data | 2-Way Meter (Electr or Gas) response including requested meter interval consumption information for a specific period. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, reading period, reading type, reading data | 13 | M-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate payload data associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter, or customer taking incorrect action that if happens in-scale may lead to serious impact to customers or the organization; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again, may wait for next time periods send of meter read data and then processing for multiple time periods; |
| NIC_firmware_update_broadcast_cmd | cmd | Operations e.g. MDMS actor sends command to initiate a firmware update on a large body of meter NICs. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | timeout, firmware version number cut over time or cut over parameters, firmware update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| NIC_firmware_update_cmd | cmd | AMI Head-End and/or Field Tool sends command to initiate a firmware update on a single meter NIC. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| NIC_firmware_update_confirmation | resp-data | Meter sends confirmation of completion of NIC firmware upgrade to MDMS and/or Field Tool. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, success or fail notification, firmware revision information | 13, 20 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update confirmation, with device ID, firmware version number and cut over information. I - Inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - Failed firmware updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| NIC_firmware_update_multicast_cmd | cmd | AMI Head-End sends command to initiate a NIC firmware update to a defined group of meter NIC. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device group ID, timeout, firmware version number, cut over time or cut over parameters, firmware update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with Group device ID, firmware version number and cut over information. I - Inaccurate device Group ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| NIC_program_update_broadcast_cmd | cmd | AMI Head-End sends command to initiate a program update on a large body of meter NIC. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | timeout, program version number, cut over time or cut over parameters, program update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| NIC_program_update_cmd | cmd | AMI Head-End and/or Field Tool sends command to initiate a meter program update on a single meter NIC. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, timeout, program version number, cut over time or cut over parameters, program update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with device ID, firmware version number and cut over information. I - Inaccurate Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - Failed configuration/program update commands are assumed to be retried if failed without consequence. |
| NIC_program_update_confirmation | resp-data | Meter sends confirmation of completion of NIC program change to MDMS and/or Field Tool. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device ID, success or fail notification, program revision information, program update | 13, 20 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program confirmation, with device ID, acknowledgement code and cut over information. I - Inaccurate device ID , success vs fail status and configuration/program version could lead a utility to believe a system is up to date when incorrect. A - Failed configuration/programming updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| NIC_program_update_multicast_cmd | cmd | AMI Head-End sends command to initiate a NIC program change to a defined group of meter NICs. Meter is not a electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis | device group ID, timeout, program version information, cut over time or cut over parameters | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the configuration/program command with Group device ID, and cut over information. I - Inaccurate Group Device ID, configuration could lead to a device loading incorrect configuration cutover time could lead to a device updating before the system is ready. A - Failed configuration/program update commands are assumed to be retried if failed without consequence. |
| on-demand_Mtr-read_cmd | cmd | CIS/Billing - Utility or IHD or Cust EMS sends command requesting adhoc consumption information from a single meter. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. | Meter ID, reading type desired | 13, 15, 18, 20 | L-M-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate command parameters associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter, or customer taking incorrect action at the IHD or Custr. EMS; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to customer frustration and/or complaint filed with jurisdiction; |
| on-demand_Mtr-read_cmd_comm_err | comm-err | IHD or Cust EMS or DAP or AMI Head-End sends message to MDMS, NMS, and/or CIS/Billing - Utility of issue with adhoc meter read request. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. | Meter ID, failure code, sending device ID | 13, 20 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific meter may lead to an unnecessary health check of the meter and the telecomm network to the meter; A - not receiving this payload to the command may lead to multiple repeated attempts to request the on-demand meter read, which may lead to a specific customers frustration and/or complaint filed with jurisdiction; |
| on-demand_Mtr-read_cmd_err | cmd-err | Meter sends communication to IHD or Cust EMS or MDMS and NMS and/or CIS/Billing - Utility of issue with adhoc meter read request relating to metrology. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. | Meter ID, failure code, | 13, 15, 18, 20 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific meter may lead to an unnecessary health check of the meter and the associated application; A - not receiving this payload to the command may lead to multiple repeated attempts to request the on-demand meter read, which may lead to a specific customers frustration and/or complaint filed with jurisdiction, or eventually to organization observing a broken meter read application; |
| on-demand_Mtr-read_resp-data | resp-data | Meter sends communication of consumption information as requested from a adhoc meter read request to IHD or Cust EMS or MDMS and NMS and/or CIS/Billing - Utility. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. | Meter ID, reading type, reading data | 13, 15, 18, 20 | L-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate payload data associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter, or customer taking incorrect action at the IHD or Custr. EMS that if happens in scale may lead to sever impact to customers or the organization; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to customer frustration and/or complaint filed with jurisdiction; |
| otg_ntf_evnt_data | alarm | The communication from a device notifying the utility of a loss of power. | device ID, event code | 11, 12 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific device may lead to an unnecessary health check of the device; A - not receiving this payload from a specific device may lead to not having accurate information about where the electrical system outage occurred. Due to this payload originating from a device that is experiencing the outage, these messages may not be successfully sent due to a broadcast sent from the device along with other devices that are affected. |
| PHEV_price_rate_cmd | cmd | Operations e.g. LMS actor sends communication to PHEV notifying customer of PHEV price tier. | device ID, price information | 13, 15, 18 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data e.g. the PHEV base charging price rates are either published tariffs or those posted at public charging stations; I - inaccurate command parameters associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for the PHEV charge, which may lead to customer frustration and/or complaint filed with jurisdiction; A - not receiving the payload will create missing data for a PHEV charge and may trigger an immediate retry, which if fails again may lead to customer frustration and/or complaint filed with jurisdiction; |
| PHEV_price_rate_comm_err | comm-err | ESI sends communication to Operations e.g. LMS of issue with sending PHEV price tier to PHEV. | device ID, failure code | 13, 15, 18 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific EVSE/EUMD or Sub-Meter may lead to an unnecessary health check of the EVSE/EUMD or Sub-Meter and the telecomm network to the EVSE/EUMD or Sub-Meter; A - not receiving this payload may lead to multiple repeated attempts to request the PHEV price rates, which may lead to a specific customers frustration and/or filed complaint with jurisdiction; |
| PHEV_pwr_chrg_rate_comm_err | comm-err | AMI Head-End sends communication to PHEV, Operations e.g. LMS, NMS of issue with communication of PHEV power charging rate negotiation to PHEV. | device ID, failure code | 13, 15, 18 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific EVSE/EUMD or Sub-Meter may lead to an unnecessary health check of the EVSE/EUMD or Sub-Meter and the telecomm network to the EVSE/EUMD or Sub-Meter; A - not receiving this payload may lead to multiple repeated attempts to request the PHEV power charging rates, which may lead to a specific customers frustration and/or filed complaint with jurisdiction; |
| PHEV_pwr_chrg_rate_negot-thrd | negot-thrd | LMS & PHEV exchanging negotiation messages of 'Notification of relative power charging rate levels and associated price rate tiers with any avaialble DR or TOU pricing riders for PHEV. | device ID, price rate tier, power charge rate level, DR or TOU rider rates | 13, 15, 18 | L-M-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data, if any non-public DR or TOU riders then this would be a minor harm and might rise to serious harm to organization especially if in-scale; I - inaccurate payload attributes associated to a specific PHEV may lead to an unnecessary health check of the EVSE/EUMD or Sub-Meter and may lead to inaccurate PHEV charge billing or may lead to serious effect on safe reliable operation of associated meter's circuit especially if in-scale; A - not receiving this payload may lead to multiple repeated attempts to select (negotiate) the customer preferred power charging rate, which may lead to a specific customers frustration and/or filed complaint with jurisdiction; |
| PHEV_pwr_chrg_status_resp-data | resp-data | PHEV sends response to Operations e.g. LMS actor of charge status request | device ID, battery charge status (e.g. 80%, full, etc) | 13, 15, 18 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - inaccurate payload attributes associated to a PHEV may lead to an incorrect data interpretation or next workflow process execution; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to customer frustration and/or complaint filed with jurisdiction; |
| PHEV_Vin_data_cmd | cmd | PHEV sends communication to Operations e.g. MDMS actor of specific PHEV identification | device ID, VIN, command parameter | 13, 15, 18 | L-M-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data as other customer account data is not in this payload; I - inaccurate command parameters associated to a meter may lead to an incorrect data interpretation or next workflow process execution; A - not receiving the response payload to the command would create missing data for a PHEV charging attempt and may trigger an immediate retry, which if fails again may lead to customer frustration and/or complaint filed with jurisdiction; |
| PHEV_Vin_data_comm_err | comm-err | AMI Head-End sends communication to PHEV of error in sending PHEV identification to MDMS. | device ID, failure code | 13, 15, 18 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific PHEV may lead to an unnecessary health check of the PHEV or EVSE/EUMD and the telecomm network to the PHEV or EVSE/EUMDr; A - not receiving this payload may lead to multiple repeated attempts to request the PHEV Vin data, which may lead to a specific customers frustration and/or filed complaint with jurisdiction; |
| Power_Quality_Event | alarm | Meter sends to MDMS any number of Power Quality alerts/alarms e.g. out-of-state or passed theshold conditions e.g. leading/lagging power, voltage fluxuactions, inbalance in energy flow, harmonics, sags, swells | Meter ID, alarm code | 13 | M-H-H | C - minimal to sever harm to organization for not showing good stewardship (unauthorized access to/disclosure) of customer meter and electrical characteristics data; I - a false negative or false positive alarm code associated to a specific meter may lead to an incorrect next workflow process execution that may lead to serious to catastrophic effect on safe reliable operation of the meter or associated meter's circuit; A - not receiving this payload from a specific meter might lead to lead to an inappropriate action/operation being taken that may have a serious to catastrophic effect on safe reliable electric operation of the meter or associated meter's circuit; |
| prepay_cust_enroll_cmd | cmd | Customer sends command (via browser) notifying Service Provider (after customer authentication to secure web portal) of Customer's request to enroll in prepay program. | customer's: Account ID, cust-program code | 16 | H-M-L | C - severe to catastrophic harm to customer or organization (in scale) for access to/disclosure of payload data, probably leads to complaint filed with jurisdiction; I - inaccurate command parameters associated to an account or a batch of accounts may lead to an incorrect next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. unenrollment/re-enrollment) for specific or batches of accounts leading to severe harm to customers or organization, with likely complaints filed with jurisdiction; A - not receiving the response payload to this command would create missing data for a specific or batch of accounts and would trigger a retry by customer; may lead to customer frustration and complaint filed with jurisdiction, minor harm to organization; |
| prepay_cust_unenroll_cmd | cmd | Customer sends command (via browser) notifying Service Provider (after customer authentication to secure web portal) of Customer's request to unenroll from prepay program. | customer's: Account ID, cust-program code | 16 | H-M-L | C - severe to catastrophic harm to customer or organization (in scale) for access to/disclosure of payload data, probably leads to complaint filed with jurisdiction; I - inaccurate command parameters associated to an account or a batch of accounts may lead to an incorrect next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-enrollment/unenrollment) for specific or batches of accounts leading to severe harm to customers or organization, with likely complaints filed with jurisdiction; A - not receiving the response payload to this command would create missing data for a specific or batch of accounts and would trigger a retry by customer; may lead to customer frustration and complaint filed with jurisdiction, minor harm to organization; |
| prepay_meter_config_cmd | cmd | CIS/Billing - Utility sends command configuring meter to accept customer participation in prepay. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component | Meter ID, command code, config-parms | 13, 20 | L-H-L | C - minimum to severe harm to customer or organization (in scale) for access to/disclosure of payload data, may lead to complaint filed with jurisdiction; I - inaccurate command parameters associated to one or a batch of prepay meters may lead to an incorrect next workflow process execution that may lead to a reprogramming/reconfig of meter(s), that may lead to serious harm to customers or severe harm to organization (if-in-scale), with likely complaints filed with jurisdiction; A - not receiving the response payload to this command would create missing data for a specific or batch of prepay meters, creating meters unable to function as prepay meters, and may trigger a retry of meter reconfig it not detected, may lead to customer frustration and complaint filed with jurisdiction if customer service /billing impacted, minor harm to organization; |
| prepay_msg_[1of10]_resp-data | resp-data | CIS/Billing - Utility sends notifications (e.g. any one of ~10 different messages specific to prepay account balance, usage, and other account/payment information) to customer IHD, Cust EMS | HAN device (IHD, Cust EMS) ID, command code, display variable data (e.g. kwh, prepay $/kwh balance, estimate time to 0 balance, avg usage per period, payment amounts) | 13, 15 | M-H-M | C - minor to severe harm to organization for access to/disclosure of payload data (not demonstration ability to restrict access to data, minor harm to customer as the payload data is associated to a HAN device identifier not to an account IT or customer name; I - inaccurate data (specific to more than one account), may lead to an incorrect next workflow process execution (by Service Provider or Customer), that may lead to inappropriate service disconnect, Customer premature payments,and lost of Customer trust and increased frustration with Utility, and/or complaint filed with jurisdiction, a sever to catastrphic (if life threatening) harm to customer and service provider when in-scale; A - not receiving this payload would create stale data for a specific or batch of prepay meters and may trigger an immediate retry or retry at next file transfer period and not providing customer with adequate time to take appropriate prepay program action, may lead to severe harm to customer if service disconnect message is missed; |
| RTP_pricing-data_ack | ack | HAN device participating in the RTP program sends message to LMS or DSM for either Utility of REP, acknowledging receipt and processing of the RTP pricing data | HAN device ID, acknowledgement code | 13, 15/16 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - minimal harm to customer or organization if a false acknowledgement from the wrong HAN device is sent/received, provided not in-scale. A - Receipt of these messages need to completed in a reasonable time. |
| RTP_pricing-data_brdcst | cmd | LMS or DSM for either Utility of REP sends RTP pricing data command to all RTP enrolled HAN devices | HAN device broadcast group ID, RTP price data, RTP effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| RTP_pricing-data_cmd | cmd | LMS or DSM for either Utility of REP sends RTP pricing data command to specific RTP enrolled HAN device | HAN device ID, RTP effective time period, RTP price data | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| RTP_pricing-data_mltcst | cmd | LMS or DSM for either Utility of REP sends RTP pricing data command to specific groups of RTP enrolled HAN devices | HAN device multicast group ID, RTP price data, RTP effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| Security_Event | alarm | Meter sends notification to Operations e.g. MDMS actor of a possible security breach or related event: Tamper / tilt, bad credentials, abnormal activity reporting, Denial of service, Meter inversion, Cover removal | Meter ID, alarm code | 13, 22 | M-H-H | C - minimal to server harm to organization or Customer for not showing good stewardship (unauthorized access to/disclosure) of customer meter security and operation data; I - a false negative or false positive alarm code associated to a specific meter may lead to an incorrect next workflow process execution that may lead to serious to catastrophic effect on safe reliable operation of the meter or false claim against customer; A - not receiving this payload from a specific meter might lead to lead to an inappropriate action/operation being taken that may have a serious to catastrophic effect on safe reliable electric operation of the meter or false claim against customer; |
| ESI-In-Utility_firmware_update_broadcast_cmd | cmd | 125 | command code, firmware-update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| ESI-In-Utility_firmware_update_cmd | cmd | AMI Head-End sends command to initiate a firmware update on a single Utility ESI. ESI is not an electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, command code, firmware-update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with device ID, firmware version number and cut over information. I - Inaccurate Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| ESI-In-Utility_firmware_update_confirmation | resp-data | Utility ESIs sends confirmation to Operations e.g. MDMS actor of completion of ESI firmware upgrade. ESI is not an electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | device ID, acknowledgement code | 13, 20 | M-M-M | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update confirmation, with device ID, firmware version number and cut over information. I - Inaccurate device ID , success vs fail status and firmware version could lead a utility to believe a system is up to date when incorrect. A - Failed firmware updates confirmations are assumed to be retried if failed without consequence however confirmation is expected to be guaranteed |
| ESI-In-Utility_firmware_update_multicast_cmd | cmd | AMI Head-End sends command to initiate an ESI firmware update to a defined group of Utility ESIs. ESI is not an electric grid critical infrastructure component. This payload is not used primarily for disturbance analysis. | group ID, command code, firmware-update | 13, 20 | M-H-L | C - moderate harm to customer and utility if an adversary is able to ascertain the firmware update command, with Group device ID, firmware version number and cut over information. I - Inaccurate device Group ID, Firmware could lead to a device loading incorrect firmware, cutover time could lead to a device updating before the system is ready. A - Failed firmware updates commands are assumed to be retried if failed without consequence. |
| svc_rst_ntf_evnt_data | alert | Meter sends communication to Operations e.g. OMS actor of Meter metrology detecting power restoration. | device ID, alert code | 13 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - a false negative or false positive payload attributes associated to a specific device may lead to an unnecessary health check of the device; A - not receiving this payload from a specific device may lead to the utility not knowing with certainty if an any "nested" outages still exist after a major outage. |
| SW_opr_cancel_cmd | cmd | CIS/Billing - Utility sends communication to Meter cancelling the issuance of a previously issued switch open or close command. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, command code | 13/14 | M-H-M | C - minimal harm to individual customer, rising to serious impact (if in scale) to organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter would lead to incorrect service switch operation, and potential serious (especially if on life support) harm to customer or potentially severe harm to customer and/or Utility (if in-scale), leading to customer frustration and likely complaint filed with jurisdiction; A - not receiving this payload (and the follow-on acknowledgement) may trigger an immediate retry, which if fails again may lead to a field visit after potential serious harm to customer, leading to customer frustration and likely complaint filed with jurisdiction; |
| SW_opr_cmd | cmd | CIS/Billing - Utility sends communication to Meter issuing a service switch open or close command. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, command code | 13/14 | M-H-M | C - minimal harm to individual customer, rising to serious impact (if in scale) to organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter would lead to incorrect service switch operation, and potential serious (especially if on life support) harm to customer or potentially severe harm to customer and/or Utility (if in-scale), leading to customer frustration and likely complaint filed with jurisdiction; A - not receiving this payload (and the follow-on acknowledgement) may trigger an immediate retry, which if fails again may lead to a field visit after potential serious harm to customer, leading to customer frustration and likely complaint filed with jurisdiction; |
| SW_opr_cmd_ack | ack | Meter sends to CIS/Billing - Utility & MDMS actors of service switch command receipt/operate acknowledgment. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, acknowledgement code | 13/14 | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter might lead to incorrect next work flow task execution, or a extra meter service switch state inquiry, with minimal harm to customer or organization; A - not receiving the response payload to the command may create missing dependency for a workflow next step execution, and may trigger an immediate retry, which if fails again may lead to further meter health checks, with minimal harm to customer or organization; |
| SW_opr_cmd_comm-err | comm-err | DAP or AMI Head-End sends to CIS/Billing - Utility, MDMS, NMS service switch operate communication failure notification. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. HAN networks are not used. | Meter ID, failure code, sending device ID | 13, 20 | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - a false negative or false positive payload attributes associated to a specific meter may lead to an unnecessary health check of the meter and the telecomm network to the meter; A - not receiving this payload to the command may lead to multiple repeated attempts to request the service switch operation, which may lead to a specific customers frustration and/or complaint filed with jurisdiction; |
| SW_opr_fail_cmd-err | cmd-err | Meter sends service switch operate failure notification to CIS/Billing - Utility & MDMS. Even though Meter is not a electric grid critical infrastructure component, this payload may be used in performing meter and telecomm network diagnostics. HAN networks are not used. | Meter ID, failure code, | 13, 20 | L-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - a false negative or false positive payload attributes associated to a specific meter may lead to an unnecessary health check of the meter and the associated application; A - not receiving this payload to the command may lead to multiple repeated attempts to request the service switch operation, which may lead to a meter in an abnormal operating state that may lead to damage to the meter, which may lead to customer frustration and/or complaint filed with jurisdiction; |
| SW_post-oper-info_resp-data | resp-data | Meter sends service switch post operation metrology data to CIS/Billing - Utility & MDMS. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, Meter oper extended data | 13/14 | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate payload data associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to organization performing unnecessary meter health checks; |
| SW_state_cmd | cmd | CIS/Billing - Utility sends to Meter command requesting current state of service switch. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, command code | 13/14 | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing for that meter; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to unnecessary meter health checks; |
| SW_state_cmd_resp-data | resp-data | Meter sends response to CIS/Billing - Utility, MDMS, or LMS or DSM the meter service switch state command request. This is a grid op task not a maint task. A meter is not an electric grid critical infrastructure component. HAN networks are not used | Meter ID, response data (SW state, voltage, amps) | 13/14 | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate payload data associated to a meter may lead to an incorrect data interpretation or next workflow process execution that may lead to a partial rebuild of stored data or a reprocessing (e.g. re-billing) for that meter; A - not receiving the response payload to the command would create missing data for a meter and may trigger an immediate retry, which if fails again may lead to may lead to unnecessary meter health checks; |
| TOU_pricing-data_ack | ack | HAN device participating in the TOU program sends message to LMS or DSM for either Utility of REP, acknowledging receipt and processing of the TOU pricing data | HAN device ID, acknowledgement code | 13, 15/16 | L-L-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - minimal harm to customer or organization if a false acknowledgement from the wrong HAN device is sent/received, provided not in-scale. A - Receipt of these messages need to completed in a reasonable time. |
| TOU_pricing-data_brdcst | cmd | LMS or DSM for either Utility of REP sends TOU pricing data command to all TOU enrolled HAN devices | HAN device broadcast group ID, TOU price data, TOU effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| TOU_pricing-data_cmd | cmd | LMS or DSM for either Utility of REP sends TOU pricing data command to specific TOU enrolled HAN device | HAN device ID, TOU effective time period, TOU price data | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| TOU_pricing-data_mltcst | cmd | LMS or DSM for either Utility of REP sends TOU pricing data command to specific groups of TOU enrolled HAN devices | HAN device multicast group ID, TOU price data, TOU effective time period | 13, 15/16 | L-H-L | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them and the content of message. A - Receipt of these messages need to completed in a reasonable time. |
| valve_opr_cancel_cmd | cmd | CIS/Billing Utiltiy sends a valve open or close cancel command to 2-Way gas meter | Meter ID, cmd code |  | M-H-M | C - minimal harm to individual customer, rising to serious impact (if in scale) to organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter would lead to incorrect service valve operation, and potential catastrophic if in scale(e.g. Gas leak) harm to customer or potentially severe harm to customer and/or Utility (if in-scale); A - not receiving this payload (and the follow-on acknowledgement) may trigger an immediate retry, which if fails again may lead to a field visit after potential serious harm to customer, leading to customer frustration and likely complaint filed with jurisdiction; |
| valve_opr_cmd | cmd | CIS/Billing Utiltiy sends a valve open or close command to 2-Way gas meter | Meter ID, opr cmd, scheduled time |  | M-H-M | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter would lead to incorrect service valve operation, and potential serious (e.g. Gas leak) harm to customer or potentially severe harm to customer and/or Utility (if in-scale); A - not receiving this payload (and the follow-on acknowledgement) may trigger an immediate retry, which if fails again may lead to a field visit after potential serious harm to customer, leading to customer frustration and likely complaint filed with jurisdiction; |
| valve_opr_cmd_ack | ack | 2-Way Meter - Gas sends message to CIS/Billing Utility, acknowledging receipt and processing of the valve operate command | Meter ID, acknowlwdgement code |  | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command acknowlegements would cause the utility to not understand whether a valve was operated correctly A - not receiving the response payload to the command would cause the utility to not understand the state of the valve and would cause the utility to visit the premises in person |
| valve_opr_cmd_comm-err | comm-err | DAP sends message to Utility back-office systems, of failure to communicate with the 2-Way Meter - Gas | Meter ID, err-code |  | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command acknowlegements would cause the utility to not understand whether a valve was operated correctly A - not receiving the communication error payload to the command would cause the utility to not understand the state of the valve and would cause the utility to visit the premises in person |
| valve_opr_fail_cmd-err | cmd-err | 2-Way Meter - Gas sends message to Utility back-office systems, of failure to perform/complete the valve operate command | Meter ID, err-code |  | L-M-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate command parameters associated to a meter would lead to incorrect service valve operation, and potential serious (e.g. Gas leak) harm to customer or potentially severe harm to customer and/or Utility (if in-scale); A - not receiving this message may cause a utility to not understand business value of reducing visits to a customers premises |
| valve_post-oper-info_resp-data | resp-data | 2-Way Gas meter sends message to Utility back-office systems, of the state of the 2-Way Meter - Gas | Meter ID, device state values |  | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate valve state payloads would cause the utility to not understand whether a valve was operated correctly A - not receiving the response payload to the command would cause the utility to not understand the state of the valve and would cause the utility to visit the premises in person |
| valve_state_cmd | cmd | CIS/Billing Utiltiy sends a get valve state command to 2-Way gas meter | Meter ID cmd code |  | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate valve state payloads would cause the utility to not understand whether a valve was operated correctly A - not receiving the response payload to the command would cause the utility to not understand the state of the valve and would cause the utility to visit the premises in person |
| valve_state_cmd_resp-data | resp-data | 2-Way Meter - Gas sends message to Utility back-office systems, of the position of the valve | Meter ID, device state values |  | L-L-L | C - minimal harm to customer or organization for access to/disclosure of payload data as the payload data is tagged to a Meter ID not a customer account; I - inaccurate valve state payloads would cause the utility to not understand whether a valve was operated correctly A - not receiving the response payload to the command would cause the utility to not understand the state of the valve and would cause the utility to visit the premises in person |
| Vol_load_shed_req_ack | ack | IHD or Cust EMS or PCT sends message to LMS or DSM acknowledging customer IHD, Cust EMS, or PCT received the load management event. | device ID, mac address, acknowledgement code, event ID, estimation of load reduction | 13, 15/16, 18 | L-M-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - Caller of the load management event needs to understand the message is properly received by the intended devices. A - Receipt of these messages need to completed in a reasonable time but are not critical. |
| Vol_load_shed_reqst | cmd | LMS or DSM sends notification of voluntary load shed opportunity to Meter, IHD, Cust EMS.. | device ID, command code, duration of event | 13, 15/16, 18 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |
| Vol_load_shed_reqst_brdcst | cmd | LMS or DSM sends notification of voluntary load shed opportunity to a large group of meters, IHD, Cust EMS. | command code, duration of event | 13, 15/16, 18 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |
| Vol_load_shed_reqst_mltcst | cmd | LMS or DSM sends notification of voluntary load shed opportunity to a specific group of meters, IHD, Cust EMS. | group ID, command code, duration of event | 13, 15/16, 18 | L-H-M | C - none to minimal harm to customer or organization for access to/disclosure of payload data; I - These messages need to be properly attributed to the Energy Service Provider that sent them. A - Receipt of these messages need to completed in a reasonable time. |

# Footnotes

For additional information regarding EISA 2007,  please visit http://energy.senate.gov/public/_files/RL342941.pdf

SOURCE: NIST Smart Grid Twiki, http://collaborate.nist.gov/twiki-sggrid/bin/view/SmartGrid/PriorityActionPlans

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Interium_Release_3/

SOURCE: “NIST Framework and Roadmap for Smart Grid Interoperability Standards, Release 1.0”, page 20

http://osgug.ucaiug.org/UtiliComm/Shared%20Documents/Forms/AllItems.aspx

# Comments

The listed Use Cases do not match up with what is later listed in section 4, nor the 19 use cases listed in the Requirements Table. Need to harmonize across these areas. E.G. the Rqmts Table use cases can be mapped into the Section 4 listings, but Section 4 Use Case labels need to sync with Table 1

From NIST Interim Smart Grid Roadmap

I do not see this in the SRS Specification.

I do not recall if Substation Sensor was considered as Line Sensor.  Nothing added below until there is conformation for inclusion.

Customer meters serve as sensors for Voltage and VAR Management as well as for state estimation for DMS on-line power flow.  Nothing added below until there is confirmation for inclusion.

Most of the text below is copied from the Maintenance section above.  Excluded Alarms and Operate Failures as these would not be specific to Voltage and VAR Management.