Priority Action Plan 7:

Key Energy Storage and Distributed Energy Resources (ES-DER) Use Cases

April 2010

Table of Contents

1.	Overview	2

1.1	Conceptual Architecture: Electrical Coupling Point (ECP)	2

1.2	Direct Control of ES-DER Systems	2

1.3	Interactive Control of Autonomous ES-DER Systems	2

1.4	Broadcast or Multicast Requests to Groups of ES-DER Systems	2

1.5	Types of ES-DER Systems	2

2.	Use Cases: DER EMS Direct Interaction with Energy Storage (ES-DER)	2

2.1	Overview of DER EMS Direct Interactions	2

2.2	Actors for Direct Control Interactions	2

2.3	Use Case: Initialization of Interactions between DER EMS and ES-DER Device	2

2.4	Use Case: DER EMS Commands ES-DER Device to Charge	2

2.5	Use Case: DER EMS Commands ES-DER Device to Discharge	2

2.6	Use Case: ES-DER Status Reporting	2

2.7	Use Case: ES-DER Event/History Logging	2

3.	Use Cases: Utility Market-based Interactions with Energy Storage	2

3.1	Use Case: RTO/ISO Deployment and Real-Time Communications - Economic	2

4.	Use Cases: Utility Interactive and/or Broadcast Interactions with Energy Storage (ES-DER)	2

4.1	Overview of Interactive and/or Broadcast Interactions	2

4.2	Actors for Utility Interactions	2

4.3	Use Case: Advanced Distribution Automation (ADA) to Analyze Distribution Operations	2

4.4	Use Case: Connect / Disconnect ES-DER Inverter from Grid	2

4.5	Use Case: Request Real Power (Charge or Discharge ES-DER)	2

4.6	Use Case: Provide Pricing Signal to Charge/Discharge Storage	2

4.7	Use Case: Adjust Power Factor	2

4.8	Use Case: Volt/Var Optimization: Energy Conservation Mode	2

4.9	Use Case: Maximum Var Support Mode	2

5.	Use Cases: Scheduled Real Power and Ancillary Services Commands	2

5.1	Overview of Issuing Schedules for Real Power and Ancillary Services	2

5.2	Actors for Scheduling	2

5.3	Use Case: Scheduling for Real Power (Charge or Discharge ES-DER)	2

5.4	Use Case: Scheduling Var Modes	2

6.	Additional ES-DER Use Cases?	2

# Overview

Energy storage, by itself and in combination with distributed generation (termed ES-DER), can be coupled with inverter-based technology to act either as a load or as a generator, and to be used by their owners and by utilities for many different purposes.

In general, there are three methods to manage ES-DER units:

- Direct management by a ES-DER controller of a specific ES-DER unit: tightly coupled commands assuming complete knowledge of the ES-DER unit status and capabilities

- Interactive management of ES-DER controllers: loosely-coupled requests assuming key knowledge of current ES-DER unit status, but allowing ES-DER controller to accept, not accept, or modify the request based its internal knowledge of the ES-DER unit capabilities. The ES-DER controller provides feedback to the requester.

- Broadcasting or multicasting by utilities to many types/sizes/regions of ES-DER units: open requests without the expectation of any directly communicated responses. Only changes in the power system (voltage, vars, load level, etc.) and the eventual metering of the ES-DER unit provide feedback.

The latter two methods could issue single control requests or could provide a schedule of control requests based on time, temperature, pricing signal, or other parameters.

These different ES-DER management interactions are shown in the general ES-DER system illustrated below.

## Conceptual Architecture: Electrical Coupling Point (ECP)

Some ES-DER systems may be directly connected to the utility grid, while others may be part of a site microgrid. In either case, the ES-DER systems will have a point of electrical connection, which is defined as:

“The point of electrical connection between the DER source of energy (generation or storage) and any electric power system (EPS). Each DER (generation or storage) unit has an ECP connecting it to its local power system; groups of DER units have an ECP where they interconnect to the power system at a specific site or plant; a group of DER units plus local loads have an ECP where they are interconnected to the utility power system.

NOTE For those ECPs between a utility EPS and a plant or site EPS, this point is identical to the point of common coupling (PCC) defined in the IEEE 1547 “Standard for Interconnecting Distributed Resources with Electric Power Systems”.

This concept is illustrated in Figure 1.

Figure 1: Electrical Connection Point (ECP)

## Direct Control of ES-DER Systems

Directly controlled ES-DER systems have their components (inverters, generators, storage, etc.) directly monitored and controlled by a separate controller. With managed ES-DER systems, the intelligence that makes the DER settings and the ES charge/discharge decisions is in the separate controller. This separate controller can issue settings, get status information, monitor measured values, and command control actions of specific ES-DER systems with the expectation of communicated replies acknowledging the commands and providing the status and/or response information. This method provides tightly-coupled control, and requires active and rapid interactions between the controller and the ES-DER system.

This separate controller may receive requests and other information from external systems (such as  a customer EMS, a utility, or an energy service provider). The controller may also, depending upon its capabilities, utilize schedules of energy prices, weather forecasts, expected customer requirements for stored energy at different times, etc. to determine what direct control commands it will issue to the ES-DER system or other component.

Examples of direct commands to an ES-DER system include:

- Connect/disconnect from grid

- Charge to % of capacity at specified ramp rate or for specified length of time

- Discharge to % of capacity at specified ramp rate or for specified length of time

Pricing signal to provide information to an autonomous ES-DER system on which to make charging/discharging decisions.

The communications between such a separate controller and the components it is controlling may be proprietary if it is provided as a turn-key integrated “autonomous” system. If, however, the controller and the ES-DER system are provided separately, then communication standards should be used.

## Interactive Control of Autonomous ES-DER Systems

Autonomous ES-DER systems locally manage their own settings, including charging and discharging of storage. They use both local data and general information that may be provided to the ES-DER system.  General information might include schedules of energy prices, weather forecasts, expected customer requirements for stored energy at different times, and expected availability of locally produced energy.

An example of an autonomous ES-DER system would be a residential customer-owned PV-inverter-and-battery-storage system that is charging and discharging according to preferences set by the customer. Any communications between components of this autonomous system are handled internally and may be proprietary. Only communications between the autonomous ES-DER system and external systems would be standardized.

Interactive control of autonomous ES-DER systems therefore sets the explicit energy and ancillary services requirements for what should be provided at the ECP (electric coupling point) between the ES-DER system and the grid, but does not micromanage how or which components of the ES-DER system are use to meet those ECP requirements.

An example of interactive control of an autonomous ES-DER system would be a utility-owned PV/Storage plant that combines multiple independent PV systems with multiple different types of storage capabilities. The utility would interactively control the plant’s local EMS by providing overall ECP requirements for the plant, while the plant’s EMS would directly manage the individual ES-DER devices in order to meet those ECP requirements.

## Broadcast or Multicast Requests to Groups of ES-DER Systems

Utilities and/or energy service providers could broadcast or multicast requests to groups of ES-DER systems without setting explicit ECP requirements and without the expectation of directly communicated responses. Most importantly, these are “requests” not “controls”. This broadcast/multicast request approach is termed decentralized and/or “loosely-coupled”.

The broadcast/multicast requests could be in the form of pricing signals for energy, but could also include more precise requirements for ancillary services, such as var support, frequency regulation, and emergency actions. These requirements could be for immediate implementation or could be time-based schedules or condition-based response profiles.

Broadcasts or multicasts would be used typically for smaller ES-DER systems. For these smaller ES-DER systems, the utility would not need to get (or may not be able to get) any explicit response back from the ES-DER systems on whether or not they responded or by how much. The utility would rely primarily on aggregated response of these ES-DER systems as indicated by changes in the power system dynamics, rather than on specific communication responses by individual ES-DER systems. The results of these broadcast requests would be seen from real-time monitoring of the power grid and from eventual reading of metered information.

This is an individual design or implementation consideration, based on the need of the utility for precise results. They can see general results as they monitor the power system in real-time, and can assess more specific results much later as they get information from the metering systems.

## Types of ES-DER Systems

The following are some of the types of ES-DER systems that are covered, many of which are either combined generation/storage or could be implemented in combination with generation capabilities:

Chemical

Hydrogen

Biofuels

Liquid nitrogen

Oxy-hydrogen

Hydrogen peroxide

Biological

Starch

Glycogen

Electrochemical

Batteries

Flow batteries

Fuel cells

Electrical

Capacitor

Super capacitor

Superconducting magnetic energy storage (SMES)

Mechanical

Compressed air energy storage (CAES)

Flywheel energy storage

Hydraulic accumulator

Hydroelectric energy storage

Spring

Gravitational potential energy (device)

Thermal

Ice Storage

Molten salt

Cryogenic liquid air or nitrogen

Seasonal thermal store

Solar pond

Hot bricks

Steam accumulator

Fireless locomotive

Eutectic system

Fuel Conservation storage

# Use Cases: DER EMS Direct Interaction with Energy Storage (ES-DER)

## Overview of DER EMS Direct Interactions

Directly managed ES-DER systems have their components (inverters, generators, storage, etc.) directly monitored and controlled by a separate controller. With managed ES-DER systems, the intelligence that makes the DER settings and the ES charge/discharge decisions is in the separate controller. This separate controller can issue settings, get status information, monitor measured values, and command control actions of specific ES-DER systems with the expectation of communicated replies acknowledging the commands and providing the status and/or response information. This method provides tightly-coupled control, and requires active and rapid interactions between the controller and the ES-DER system.

## Actors for Direct Control Interactions

| Actor Name | Actor Type (person, organization, device, system, or subsystem) | Actor Description |
| --- | --- | --- |
| DER EMS | System | Energy management system, belonging to the owner or operator of the distributed energy resources (DER) Energy Storage - Distributed Energy Resource (ES-DER), that determines what actions to command the unit to perform. |
| Energy Storage - Distributed Energy Resource (ES-DER) | Device | Device that can store energy, and can be commanded to charge or discharge |

## Use Case: Initialization of Interactions between DER EMS and ES-DER Device

Narrative

The Owner of an ES-DER device has a “DER EMS” which is tasked with managing the ES-DER device.  The algorithms used by the DER EMS for determining what to command the ES-DER device to do, is outside the scope of this Use Case (see either market-based and ADA Use Cases); however, the actions taken are within the scope of this Use Case.

In the initialization process, the DER EMS needs to determine the capabilities and internal settings of the ES-DER device. Some of these capabilities are “nameplate” information, but settings can be more dynamic, reflecting the current environment or state of the device. For instance, the setting for the maximum discharge level may vary with the wishes of the owner, or with the age of storage device, or with the time of day.

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Detection of new ES-DER device installation | DER EMS | ES-DER | Handshake to establish network connection | Network information | Two-way interactions |
| 2 | Network connection established | DER EMS | ES-DER | Establish cyber security level and capabilities, and authenticate certificate | Cyber security capabilities Cyber suites supported Cyber certificate information if appropriate | Two-way interactions |
| 3a | Full connection established | DER EMS | ES-DER | Request “nameplate” and other settings information | Request for initial ES-DER information | Some of this information may be “pre-stored” in the DER-EMS as part of the installation process |
| 3b | Request for initial ES-DER information | ES-DER | DER EMS | Provide “nameplate” and other settings information | Type of ES-DER Capacity Charge level H/L limits Charging rate H/L limits Discharging rate H/L limits Inverter capabilities Other nameplate information | Some of this information may be “pre-stored” in the DER-EMS as part of the installation process |
| 4a | Request for electrical interface status | DER EMS | ES-DER | Request status information of electrical interface | Request for electrical interface status | Some of this information may be “pre-stored” in the DER-EMS as part of the installation process |
| 4b | Provide electrical interface status | ES-DER | DER EMS | Provide status information of electrical interface | Nominal voltage Current Volt/var limits of inverter | Some of this information may be “pre-stored” in the DER-EMS as part of the installation process |
| 5a | Request for ES-DER status | DER EMS | ES-DER | Request status information of ES-DER | Request status information of ES-DER |  |
| 5b | Provide ES-DER status | ES-DER | DER EMS | Provide status information of ES-DER | On/off Remaining capacity Current charging/discharging rate Any alarms or errors |  |

## Use Case: DER EMS Commands ES-DER Device to Charge

Narrative

The Owner has a “DER EMS” which determines that it is beneficial to store energy and also what the most appropriate charging rate is.  The algorithms used by the DER EMS for these two determinations is outside the scope of this Use Case (see either market-based and ADA Use Cases); however, the actions taken are within the scope of this Use Case.

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1a | DER EMS decision | DER EMS | ES-DER | Request status of ES-DER | Command for status of ES-DER | If report-by-exception is available, this request may have already been reported. |
| 1b | Request for status | ES-DER | DER EMS | Send status information of ES-DER | On/off Remaining capacity Current charging/discharging rate Any alarms or errors | Assumption is that all nameplate and settings information is already known |
| 2a | No significant alarms or errors | DER EMS | ES-DER | Command to start or continue charging at a specific rate | Charge command Rate of charge | Alarms, such as ES-DER is already fully charged, will prevent this action |
| 2b | Charge command | ES-DER | DER EMS | Acknowledgement | Successful, or Error, with identification of error | Common types of errors will need to be standardized Handling errors is outside the scope of this Use Case |

## Use Case: DER EMS Commands ES-DER Device to Discharge

Narrative

The Owner has a “DER EMS” which determines that it is beneficial to discharge energy and also what the most appropriate discharging rate is.  The algorithms used by the DER EMS for these two determinations is outside the scope of this Use Case (see either market-based and ADA Use Cases); however, the actions taken are within the scope of this Use Case.

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1a | DER EMS decision | DER EMS | ES-DER | Request status of ES-DER | Command for status of ES-DER | If report-by-exception is available, this request may have already been reported. |
| 1b | Request for status | ES-DER | DER EMS | Send status information of ES-DER | On/off Remaining capacity Current charging/discharging rate Any alarms or errors | Assumption is that all nameplate and settings information is already known, so that available capacity can be calculated |
| 2a | No significant alarms or errors | DER EMS | ES-DER | Command to start or continue discharging at a specific rate | Discharge command Rate of discharge | Alarms, such as ES-DER is already at discharge limit, will prevent this action |
| 2b | Discharge command | ES-DER | DER EMS | Acknowledgement | Successful, or Error, with identification of error | Common types of errors will need to be standardized Handling errors is outside the scope of this Use Case |

## Use Case: ES-DER Status Reporting

Narrative

Many utility and/or DER EMS functions require the status of the ES-DER either periodically, on significant change of a value, or upon request.

The following status data is mandatory:

- ES-DER on or off

- Storage available or not available

- Inverter/converter active power output

- Inverter/converter reactive output

- Storage remaining capacity (% and/or kW?) (if storage is available)

The following data can optionally be reported:

- ES-DER inverter/converter status:

  - Current connect mode:  connected or disconnected at its ECP

  - Inverter on, off, and/or in stand-by status: inverter is switched on (operating), off (not able to operate), or in stand-by mode, namely capable of operating but currently not operating

  - DC current level available for operation: there is sufficient current to operate

  - Value of the output power setpoint

  - Value of the output reactive power setpoint

  - Value of the power factor setpoint as angle (optional)

  - Value of the frequency setpoint (optional)

- Power measurements:

  - Total Active Power (Total P): Value, High and Low Limits

  - Total Reactive Power (Total Q): Value, High and Low Limits

  - Average Power factor (Total PF): Value, High and Low Limits, and averaging time

  - Phase to ground voltages (VL1ER, …): Value, High and Low Limits

- ES-DER storage: e.g. battery status (if storage is battery or battery-equivalent):

  - Conditions of usage, e.g. desired schedule (preferred time of discharge, price triggers for charging/discharging, etc)

  - Amp-hour capacity rating

  - Minimum resting amp-hour capacity rating allowed

  - Nominal voltage of battery

  - Maximum battery discharge current

  - Maximum battery charge voltage

  - High battery voltage alarm level

  - Low battery voltage alarm level

  - External battery voltage

  - Rate of output battery voltage change

  - Internal battery voltage

  - Battery drain current

  - Internal battery current

  - State of charge (energy % of maximum charge level)

  - Reserve (Minimum energy charge level allowed, % of maximum charge level)

  - Available Energy (State of charge – Reserve)

  - Intermittency ramp rate

  - Maximum generation setting

- ES-DER storage: pumped hydro

  - TBD (storage status information needed for each type of ES-DER device)

- General information

  - Time resolution and source of time synchronization

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1a | DER EMS need for status of ES-DER | DER EMS | ES-DER | Request status of ES-DER | Command for status of ES-DER Identity of the group of status information desired | If report-by-exception is available, changes in this information will be continuously reported. |
| 1b | Request for status | ES-DER | DER EMS | Send status information of ES-DER | On/off Remaining capacity Current charging/discharging rate Any alarms or errors | See list in Narrative for additional types of status information that could be requested |
| 1c | If request failed | ES-DER | DER EMS | Error, failure of request | Failed (plus reason : equipment not available, message error, overridden) |  |
| 2 | Report by exception | ES-DER | DER EMS | Report any alarms, limits exceeded, errors, or other anomalies | Values being reported by exception | With tightly coupled interactions, the ES-DER can report alarms and problems without waiting to be asked |

## Use Case: ES-DER Event/History Logging

Narrative

Event/history logs are maintained by the ES-DER systems to record key timestamped events in a “circular file” that will rollover itself as new events are added. The event log can be read by selecting time ranges, including “all”, “from time xx to time yy”,  and “from time xx to the most recent event”. Once read, they could be further filtered by type of event or other criteria.

Different users of ES-DER systems will need varying timeframes for retrieving event log information and different types of information from these event logs:

- Utility operations will typically only need key operations-related information, possibly infrequently or only under special circumstances.

- Owners/managers (including utility owners) will want more detailed information, probably periodically or after certain types of events.

- Energy management systems with tightly-coupled interactions will need complete event logs relatively frequently.

- Larger ES-DER plants are different from large numbers of small ES-DER systems: more types of event data may be collected from these larger plants, while only basic event data may be collected from the smaller ES-DER systems. Larger plants may also aggregate and/or amalgamate events from multiple individual ES-DER devices.

Given this broad range of different requirements for event logs, this specification will define the following:

- An optional set of events that do not necessarily need to be implemented, but if they are implemented, then they will be implemented as specified, thus making them interoperable.

- Other types of events can be implemented for specific implementations, specific vendors, regional requirements, etc. These will not be described in this specification, but will be left to those specific implementations to define. These will therefore not necessarily be interoperable.

These events will include standardized event codes. Different users can then retrieve specific types of events and also filter the event logs through these event codes.

All event logs will contain the following fields:

- Date and time stamp: The accuracy of this timestamp will be determined by the frequency of time synchronization and the innate precision in keeping time of the ES-DER system, and is therefore outside the scope of this specification

- Data reference: the reference to the data item that triggered the event log entry

- Value: Data value field for data element that is triggering the event

- Event code: Code to uniquely identify the type of event

- Optional text field: Text of supporting information. This text will not be standardized, but can be used to provide additional details about the event.

Although not mandatory, in general it is expect that the following types of events will be logged:

- All errors or failures

- All startup and shutdown actions

- All control actions

- All responses to control actions

- All limit violations, including returns within limits

The standardized events to be captured in ES-DER system event logs are:

- Requests/commands received from utility, 3rd party, or DER-EMS, indicating type of request/command and source

- Action in response to requests/commands received, indicating type of request/command and any errors.

- Deviations from scheduled requests/commands

- Power out

- Power on

- Power trip action due to excessive power, temperature limits exceeded, inadequate DC bus voltage, etc.

- Exceeding any 1547 parameters

- Return within 1547 parameters

- Exceeding voltage limits

- Return within voltage limits

- Equipment hardware failure, indicating what equipment

- Software errors, indicating what software

- Communication failure (needs more definition on what this implies)

- Message errors, indicating what message

- Exceeding temperature limits

- Return within temperature limits

- Exceeding voltage distortion limits beyond 1547 parameters

- Exceeding current harmonic limits

- EMI events

- Time synchronized, including difference between old time and new time

- Event log error

- Event log entries overwritten without having been retrieved

- Record of all control actions of inverters resulting from requests, schedules, or crossing an internal control threshold

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1a | DER EMS need for event log of ES-DER | DER EMS | ES-DER | Request event log of ES-DER | Command for event log of ES-DER Time range for events Retrieval criteria: Event codes of the desired types of events | Time range: Start time/ stop time (start time = 0 means start from beginning of log; stop time = 0 means include through the final log entry) Retrieval criteria: event codes to be retrieved, with “wildcard” capabilities |
| 1b | Request for event log information | ES-DER | DER EMS | Send event log per retrieval criteria | Requested event log entries Success/failure indication | See list of types of events under Narrative |
| 1c | If request failed | ES-DER | DER EMS | Error, failure of request | Failure (plus reason: no log event fulfills the retrieval criteria, log not available, message error, etc.) |  |
| 2 | Notification if event log is almost full or completely full without having been retrieved | ES-DER | DER EMS | Notification if event log is almost full or completely full without having been retrieved | Notification of event log state |  |
| 3 | Notification of an event log error | ES-DER | DER EMS | Notification of an event log error | Notification of event log error |  |

# Use Cases: Utility Market-based Interactions with Energy Storage

## Use Case: RTO/ISO Deployment and Real-Time Communications - Economic

Narrative

The wholesale electricity market is operated by RTOs/ISOs to provide market-based energy and ancillary services to the bulk power system. This key Use Case covers the actual interactions between the RTO/ISO system operator and the ES-DER systems; other Use Cases in the set of Utility Market-based Interactions Use Cases cover the non-operational interactions, namely enrollment/qualification of ES-DER, scheduling/awarding market bids of ES-DER, and eventual measurement and performance evaluation.

This key Use Case, the Deployment and Real-Time Communication Use Case, describes the process for real-time communications to storage resources providing market-based services on a real-time basis and dispatch for reliability-based (emergency) response programs. The process flows and descriptions reflect a sequential process solely for the purpose of describing the real-time data flow; the real-time communication process iteratively scans and updates in the same step.

The process begins when the SO evaluates real-time system conditions through its market clearing process.

The resulting resource-specific real-time dispatch information is transformed into dispatch instructions by the SO.

If the dispatch instruction is for Regulation, the SO sends the Regulation signal to the DDE.

If the dispatch is not for Regulation, the SO sends the dispatch instruction to the DDE.

The DDE communicates with the SP through the proprietary communication system of the DDE.

The SO collects real-time response from the DDE for evaluating the next interval and uses the information to calculate the system state.

System conditions are made available to the market clearing process for the next interval and to Deployment and Real-Time Communications – Reliability.

Actors

| Actor Name | Actor Type (person, organization, device, system, or subsystem) | Actor Description |
| --- | --- | --- |
| Service Provider (SP) | Organization, System | A role which carries the responsibility of coordinating resources to deliver electricity products and services to a market or distribution operator. |
| Designated Dispatch Entity (DDE) | Organization, System | A role which carries the responsibility of receiving and processing demand resource dispatch instructions or market information and (optionally) providing response information. |
| Load Serving Entity (LSE) | Organization, System | A role which carries the responsibility of serving end-users and selling electric energy to end-users. |
| Metering Authority (MA) | Organization, System | A role which carries the responsibility of providing electric usage data necessary to determine the performance of a Resource. |
| Scheduling Entity (SE) | Organization, System | A role which carries the responsibility of submitting bids/offers and receives Schedules and Awards. |
| System Operator (SO) | Organization, System | A System Operator is a Balancing Authority, Transmission Operator, or Reliability Coordinator whose responsibility is to monitor and control an electric system in real time (based on NERC definition). The System Operator is responsible for initiating Advance Notifications, Deployment, and Release/Recall instructions. Dynamic optimization and digital monitoring and control, which are the core requirements of the Smart Grid concept, imply automated actions dealing with a large amount of data and sophisticated analyses. The System Operator responsibilities will mainly be to setup the systems, authorize the utilization of the control systems and monitor their performance based on given criteria. In the most of the situations, the operator will be outside the near-real time loop of control. |
| Transmission/Distribution Service Provider (T&D SP) | Organization, System | A role which carries the responsibility of operating a local electricity transmission and/or distribution system. |

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Market interval: time to clear market | System Operator | System Operator | Evaluate real-time conditions. | Monitored information from power system Analysis information | These actions are internal to the System Operator, and typically occur once an hour. In the Smart Grid environment, this evaluation comes from the dynamic optimization of the operating conditions, e.g., OPF or SCD, etc. The periodicity should be defined by the ability and reasonability for WASA and control. |
| 2a | Analysis results indicate need for regulation | System Operator | Designated Dispatch Entity | Issue regulation instructions | Regulation signal | Steps 2 through 4 are 24x7, iterative interactions, taken every few seconds |
| 2b | Analysis results do not need regulation | System Operator | Designated Dispatch Entity | Issue dispatch instructions | Dispatch instruction |  |
| 3 | Dispatch instructions received from System operator | Designated Dispatch Entity | Service Provider | Issue regulation and other dispatch instructions | Dispatch instructions | This action is generally one-way – it is expected that monitoring of the power system will provide the necessary feedback |
| 4 | Continuous monitoring of power system | Designated Dispatch Entity | System Operator | Provide power system monitored information | Power system information | This information is used during the next market-clearing process |

Activity Diagram

Figure 2 - Deployment and Real-Time Communications – Economic

# Use Cases: Utility Interactive and/or Broadcast Interactions with Energy Storage (ES-DER)

## Overview of Interactive and/or Broadcast Interactions

Interactive control of autonomous ES-DER systems sets the explicit energy and ancillary services requirements for what should be provided at the ECP (electric coupling point) between the ES-DER system and the grid, but does not micromanage how or which components of the ES-DER system are use to meet those ECP requirements.

If the interactive control commands are initiated by utilities, the only ECP of interest to the utility is the PCC (point of common coupling) between the ES-DER system and the utility power system. Energy service providers may manage PCCs, but may also manage ECPs within a campus, building, or other non-utility owned facilities.

Utilities and/or energy service providers could broadcast or multicast requests to groups of ES-DER systems without setting explicit ECP (PCC) requirements and without the expectation of directly communicated responses. Most importantly, these are “requests” not “controls”.

In both interactive “control” interactions and broadcast/multicast “request” interactions, the utility or energy service provider provides precise requirements for the output at the ECP (PCC) – with the expectation that ES-DER systems under interactive controls WILL meet those ECP (PCC) requirements, while ES-DER systems under broadcast requests MAY meet those ECP (PCC) requirements.

## Actors for Utility Interactions

| Actor Name | Actor Type (person, organization, device, system, or subsystem) | Actor Description |
| --- | --- | --- |
| Distribution Operator | Person | Person in charge of distribution operations during the shift |
| Distribution SCADA | System | DSCADA collects data from IEDs beyond the fence of the T&D substation and supports remote control of controllable devices in the field either in supervisory or close-loop modes. The field IEDs include utility DER and Micro-grid controllers, may include customer EMS. |
| Transmission SCADA/EMS | System | SCADA/EMS collects data from IEDs within the T&D substation and supports remote control of controllable devices in the substation. The EMS runs the applications for analysis and control of the transmission and generation systems. |
| Aggregator/ Energy Services Provider | Organization | A person or company combining two or more customers into a single purchasing unit to negotiate the purchase of electricity from retail electric providers, or the sale to these entities. The transaction may include electricity consumption and demand, DER/Micro-grid generation, Demand Response “Nega-watts”, and ancillary services. Aggregators also combine smaller participants (as providers or customers or curtailment) to enable distributed resources to play in the larger markets. |
| 3rd Party, External Systems (e.g. Weather) | Systems | Public information systems outside the utility, provides the utility with information on weather and major event relevant to utility operations. |
| DMS (Distribution Management System) | System | A set of integrated IT systems and ADA applications supporting the operations, maintenance, and planning of the electric distribution system |
| DMS Gateway | Sub-system | Computer-based system consisting of Graphic User Interface, interface with distribution SCADA, and ADA applications |
| Customer EMS | System | A customer supplied system for monitoring and managing energy use at their residence or business. It includes human interface displays for interacting with the system and allows the customer to program functions, control loads, and display energy costs, usage, and related information. It can be programmed to take action based upon price inputs or event messages from the utility, or changes to customer’s load. Interfaces with HAN devices and the Smart Meter |
| DER EMS (DER controller/gateway) | Device | Measures, stores and communicates current generation, generation schedules, capability curves, protection settings, mode of operations and voltage/var control settings, and other data needed for current and predictive model of DER operations |
| PCC interconnection controller at ECP (PCC) | Device | Calculates, stores, and communicates aggregated load, Demand Response, Generation data for the Micro-grid, Protection settings and settings for frequency and voltage control for connected and for autonomous modes of operations, other data needed for current and predictive model of Micro-grid operations. |
| Smart Meter | Device | Advanced electric revenue meter capable of two-way communications with the utility. Serves as a gateway between the utility, customer site, and customer’s load controllers. Measures, records, displays, and transmits data such as energy usage, generation, text messages, and event logs to authorized systems and provides other advanced utility functions. |
| Customer appliances, embedded in customer premises | Devices | Equipment and systems at the customer site that could participate in demand response and other programs |
| ES-DER (DER, PEV, and Electric Storage embedded in customer premises) | Devices | Equipment and systems at the customer site that could participate in demand response and other programs |
| AM/FM/GIS | System | Repository of distribution system assets, their relationships (connectivity), ownerships, nominal states, and links to associated objects. |
| Connectivity and facility parameters validation processor | Application | GIS information should be validated on two levels: 1) validation of connectivity and distribution transformer loading, and 2) integrated validation on operational reasonability. |
| Customer Information System (CIS) | System | Customer information including billing data, customer types, links to distribution circuits |
| DER data management system | System | A specific database for DER attributes, behavioral models, contracts, and performance associated with the owner. |
| AMI Data Management System | System | Gathers, validates, estimates, and permits editing of meter data such as energy usage, generation and meter logs. Stores this data for a limited amount of time before it goes to the Meter Data Warehouse and makes the data available to authorized systems. Includes load model processor and secondary equivalent processor. |
| Load Management/Demand Response System | System | Executes and monitors requested demand response resources. Sends out demand response event notifications to Smart Meters and customers. Controls DR, DER, PEV and ES charging/discharging. |
| Demand Response Data Management System | System | Stores and processes data on load management/Demand Response programs, contracts, relevant historic information, creating behavioral models for Demand Response. |
| DOMA | Application | Distribution Operation Model and Analysis is an advanced DA application. It runs periodically and by event; models near real-time power flow; Provides situational awareness of distribution operations; Provides background models for other ADA applications. |
| VVWO | Application | Volt/var/Watt Optimization is an ADA application. It runs periodically and by event; optimizes states of voltage, var, DER, Micro-grid controllers, and Demand response means; |
| FLIR | Application | Fault Location, Isolation, and Service Restoration. An ADA application. Identifies and locates the fault, isolates the faulted element from healthy sections and restores services to the customers connected to the healthy sections. Assesses, for the duration of repair, the situation with loads, DER, Demand response and Micro-grids |
| Field Crew | Persons | Manual operations of field devices, repair, construction work, patrolling and other assignment in the field |
| Market Operation System (MOS) | System | Wide-area energy market management system providing high-level market signals for DisCos |
| ISO/RTO | Systems | ISO: An independent entity that controls a power grid to coordinate the generation and transmission of electricity and ensure a reliable power supply. RTO: An independent organization that coordinates, controls, and monitors the operation of the electrical power system and supply in a particular geographic area; similar to Independent System Operator. |
| Engineering | Person | Planning, and DMS maintenance personnel, power quality and reliability engineers, etc. |
| PEV Charger | Device | The charger can either be on-board the vehicle or off-board. On-board chargers require AC energy transfer to the vehicle (either 120 or 240V single phase) and Off-board chargers are within the EVSE and require DC energy transfer to the vehicle. |
| Customer | Person | Customer is the operator of a PEV and an electric customer of the home utility. Customer enrolls in an electric utility PEV program and has selected a PEV rate tariff. Customer is responsible for connecting PEV to an Energy Portal for charging. |
| Customer Account | System | Customer Account is assigned to Customer to collect charges for billing of energy usage |
| Electric Vehicle Supply Equipment (EVSE) | Device | PEV connects to the grid using an Electric Vehicle Supply Equipment (EVSE). Electric Vehicle Supply Equipment (EVSE) is the physical electrical cord and connectors that are specified by applicable SAE standards (e.g., SAE 2293, J1772 ™, J2836 & J2847.) that provide transfer of electrical energy from energy portal to PEV. This can be 120V or 240V AC depending upon connection. |
| ESI | System | Energy Services Interface – Provides security and, often, coordination functions that enable secure interactions between relevant Home Area Network Devices and the Utility. Permits applications such as remote load control, monitoring and control of distributed generation, in-home display of customer usage, reading of non-energy meters, and integration with building management systems. Also provides auditing/logging functions that record transactions to and from Home Area Networking Devices. |
| Guest | Person | Guest is a friend or family member who has permission to use a Customer Premise for charging a PEV. May be liable for PEV charging costs depending upon Customer preferences set up within PEV program. |
| PEV, EV, PHEV | System | Plug-in Electric Vehicle (PEV). Plugs into an Energy Portal (see actor definition below) at a premise to charge vehicle. A PEV is also an EV (Electric Vehicle) that relies only on electric propulsion. A PEV is also a PHEV (Plug-In-Hybrid Vehicle) that also includes an alternative source of propulsion power. |

## Use Case: Advanced Distribution Automation (ADA) to Analyze Distribution Operations

Narrative

The objectives of Advanced Distribution Automation (ADA) functions in the Smart Grid Environment are to provide situational awareness and dynamic optimization of operations of Active Distribution Networks to enhance the reliability of power system service, power quality, power system efficiency, and cyber security, by automating data preparation in near-real-time; optimizing decision-making; and controlling distribution operations in coordination with transmission and generation systems operations. In addition to using more traditional SCADA systems, substation systems, and feeder equipment, the ADA functions will also utilize and support other Smart Grid technologies to achieve these objectives, such as:

- Advanced Metering Infrastructure (AMI)

- Distributed resources and generation, including renewable resources (DER)

- Demand response (DR)

- Advanced electricity storage, including plug-in electric and hybrid electric vehicles (ES-DER and PEV)

- Provision to consumers of timely energy, pricing, and market information, along with decision and control options for responding to this information with energy and ancillary services

Scope: The ADA Function performs a) data gathering, along with data consistency checking and correcting; b) integrity checking of the distribution power system model; c) periodic and event-driven system modeling and analysis; d) current and predictive alarming; e) contingency analysis; f) coordinated Volt/Var/Watt optimization: g) fault location, isolation, and service restoration; h) multi-level feeder reconfiguration; i) pre-arming of RAS and coordination of emergency actions in distribution; j) pre-arming of restoration schemes and coordination of restorative actions in distribution, and k) logging and reporting. These processes are performed through direct interfaces with different databases and systems, (AMI, EMS, OMS, CIS, MOS, SCADA, AM/FM/GIS, AMS, WMS, and other internal and external to the power utility IT systems), comprehensive near real-time simulations of operating conditions, near real-time predictive optimization, and actual real-time control of distribution operations.

Rationale: By meeting its objectives in near-real time, the ADA functions make a significant contribution to sustainability of the ADN and to improving the power system operations, which cannot be achieved using non-automated operational methods.

Status: The methodology and specification of the ADA function for current power system conditions have been developed, and prototype (pilot) and system-wide project in several North-American utilities have been implemented.  The applications need significant upgrades to meet the Smart Grid requirements.  This document presents the ADA functions with the upgrades suggested for meeting these requirements.

The ADA functions include the following closely coordinated applications:

- Real-time Distribution Operation Model and Analysis (DOMA)

- Fault Location, Isolation and Service Restoration (FLIR)

- Voltage/Var/Watt Optimization (VVWO)

- Distribution Contingency Analysis (DCA)

- Multi-level Feeder Reconfiguration (MFR)

- Relay Protection Re-coordination (RPRC)

- Pre-arming of Remedial Action Schemes (PRAS)

- Coordination of Emergency Actions (CEmA)

- Coordination of Restorative Actions (CRA)

- Intelligent Alarm Processing (IAP)

Steps

This very extensive Use Case covers more than ES-DER and is described in PAP 8: http://collaborate.nist.gov/twiki-sggrid/pub/SmartGrid/PAP08DistrObjMultispeak/Distribution_Grid_ManagementSG_UC_nm.doc. The ES-DER Use Cases supplement those DGMI_SG Use Cases by describing ES-DER-related details of the more general steps. At some point, these Use Cases should be integrated (or linked) to develop the bigger picture of the needed information support for the power system operations.

For ES-DER, these ADA functions help determine what pricing signals or direct commands should be sent to which types and groups of ES-DER devices. The simplified interactions between the ADA functions and ES-DER are provided below.

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically and/or upon power system alarm/event | Distribution SCADA | DMS | Request that the DMS update the requirements for efficient and reliable operation of the power system, using the DOMA (operations model) and other ADA applications | Update request Most recent power system status and measurements | If periodic, this updating will be essentially continuous, possibly every few minutes If upon an alarm or event, additional data may be required from the SCADA, depending upon the type of event |
| 2 | Request to update power system model | DER data management system | DMS | Provide any changes or new information on DER (and ES-DER) capabilities | ES-DER attributes ES-DER behavioral models Contractual capabilities and agreements (e.g. control or request) Performance/expected response from ES-DER |  |
| 3a | Completion of ADA application analyses | DMS | Aggregator/ Energy Services Provider | Issue control commands to ESP | Updated ECP (PCC) requirements | Many of the ECP (PCC) requirements are described in subsequent Use Cases |
| 3b | Control command issued | Aggregator/ Energy Services Provider | DMS | Success/fail response from ESP | Response to ECP (PCC) requirements control command |  |
| 4a | Completion of ADA application analyses | DMS | DER EMS | Issue control commands to each DER EMS under interactive control contracts | Updated ECP (PCC) requirements | Many of the ECP (PCC) requirements are described in subsequent Use Cases |
| 4b | Control command issued | DER EMS | DMS | Success/fail response from DER EMS | Response to ECP (PCC) requirements control command |  |
| 5a | Completion of ADA application analyses | DMS | DER EMS | Issue broadcast requests to each DER EMS under “demand response” contracts | Updated ECP (PCC) requirements | Many of the ECP (PCC) requirements are described in subsequent Use Cases |
| 5b | Request issued | DER EMS | DMS | Success/fail response from some DER EMS – none expected from others | Response to ECP (PCC) requirements request |  |
| 6 | Continuous | PCC interconnection controller at ECP (PCC) | Distribution SCADA | Provide status and measurements at the PCC | Status and measurements from some PCCs |  |

## Use Case: Connect / Disconnect ES-DER Inverter from Grid

Narrative

This function causes the ES-DER system to immediately physically connect or disconnect from the grid via a disconnect switch at the ES-DER system’s ECP to the grid.

- Issue Connect/Disconnect Command to ES-DER system:

  - Binary command to open or close a switch.

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status, such as closing the switch to reconnect to the grid (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus resulting switch position)

  - Rejected (plus reason: equipment not available, message error, overridden)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Alarm or event | Distribution SCADA | DMS | Request for ADA applications to assess the alarm or event to determine if ES-DER connect/disconnect (or other) actions are needed | Alarm/event information Appropriate SCADA information |  |
| 2a | ADA assessment results | DMS | DER EMS | Control command to disconnect selected ES-DER systems at ECP (PCC) | Disconnect command Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately (optional – if not included, then default time window for this function will be used) Timeout period, after which the ES-DER system will revert to its default status, such as closing the switch to reconnect to the grid (optional – if not included, then default timeout period for this function will be used) |  |
| 2b | Command receipt | DER EMS | ES-DER (or switch at ECP) | Disconnect command at the time calculated by picking a random time during the time window | Disconnect command |  |
| 2c | Command receipt | DER EMS | DMS | If permitted, respond back to DMS on actions taken on the command | Successful (plus resulting switch position) Rejected (plus reason: equipment not available, message error, overridden) | Responses expected in interactive control interactions, but not necessarily in broadcast/multicast interactions |
| 2d | After default timeout period | DER EMS | ES-DER (or switch at ECP) | Reconnect after timeout and no counter command received | Connect command |  |
| 2e | Command receipt | DER EMS | DMS | If permitted, respond back to DMS on actions taken when timeout occurred | Reconnected after timeout | Responses expected in interactive control interactions, but not necessarily in broadcast/multicast interactions |
| 3a | ADA assessment results | DMS | DER EMS | Control command to connect ES-DER at ECP (PCC) | Connect command Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately (optional – if not included, then default time window for this function will be used) |  |
| 3b | Command receipt | DER EMS | ES-DER (or switch at ECP) | Connect command at the time calculated by picking a random time during the time window | Connect command |  |
| 3c | Command receipt | DER EMS | DMS | If permitted, respond back to DMS on actions taken on the command | Successful (plus resulting switch position) Rejected (plus reason: equipment not available, message error, overridden) | Responses expected in interactive control interactions, but not necessarily in broadcast/multicast interactions |

## Use Case: Request Real Power (Charge or Discharge ES-DER)

Narrative

This function requests the storage system to charge or discharge and at what rate (% of max charging rate).  A controller might use this command frequently, in conjunction with reads of the battery charge level, to achieve a desired daily charge / dump characteristic.

To account for diversity in the size of storage systems, the function requests a percentage quantity based on the capacity of the system.  For real power out requests (storage discharging), the percent is relative to the maximum discharge rate (inverter capacity).  For real power in requests (storage charging), the percent is relative to the maximum charging rate (battery charger capacity).  It is acknowledged that the discharging capacity of the inverter and the charging capacity of the charger may differ.

A timeout period is included for reverting to the default state of the ES-DER system, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

The ES-DER system may also determine if only ES-DER system output is used for charging or whether grid power can be used.

The utility/ESP or the Customer EMS takes the following actions:

- (Optional) Request status of ES-DER system: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status (see Function PC6 for details of status points).

- Issue command to request real power (charge/discharge) setpoint for the storage system:

  - Command to adjust the real power charge/discharge setpoint for the storage system

  - Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status (optional – if not included, then default timeout period for this function will be used)

  - Storage charge from grid setting (yes/no)

- Receive response to the command:

  - Successful (plus actual real power setpoint)

  - Rejected (plus reason: equipment not available, message error, overridden)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to assess the alarm or event to determine if real power increase or decrease is needed for selected ES-DER | Event information Appropriate SCADA information | The event may be that significant power system changes have occurred near the selected ES-DER, thus changing power system efficiency or reliability |
| 2a | Real power increase or decrease is needed for selected ES-DER | DMS | DER EMS | Request status of ES-DER to determine whether they can change their real power enough | Request for status and real power measurement information | This step is optionally used in direct interactions, but cannot be used in broadcast/multicast interactions |
| 2b | Status request | DER EMS | ES-DER | Request status | Request for status and real power measurement information |  |
| 2c | Response to status request | ES-DER | DER EMS | Response to status request | ES-DER status and real power measurement information |  |
| 2d | Response to status request | DER EMS | DMS | Response to status request | ES-DER status and real power measurement information | Only if Direct Interactions are established between DER EMS and DMS |
| 3a | Real power increase or decrease is needed for selected ES-DER | DMS | DER EMS | Request selected ES-DER to change their real power at the ECP | Request to adjust the real power (percentage of nominal) at ECP Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, Timeout period, after which the ES-DER system will revert to its default status, such as resetting the real power setpoint to its default value Storage charge from grid setting (yes/no) | The three additional parameters are optional: If ramp rate not included, then use previously established default ramp rate If time window not included, then default time window for this function will be used If timeout not included, then default timeout period for this function will be used |
| 3b | Real power change request | DER EMS | ES-DER | Command ES-DER to change real power | Command to adjust real power (percentage of nominal) at requested ramp rate | DER EMS can issue commands to ES-DER |
| 3c | Response to real power change request | ES-DER | DER EMS | Response to change real power command | Successful (plus actual real power value) Rejected (plus reason: equipment not available, message error, overridden) |  |
| 3d | Response to real power change request | DER EMS | DMS | Response to change real power command | Successful (plus actual output real power value) Rejected (plus reason: equipment not available, message error, overridden) | Optional step – only if direct interactions are used. |

## Use Case: Provide Pricing Signal to Charge/Discharge Storage

Narrative

This function provides a pricing signal (actual price or some relative pricing indication) from which the ES-DER system may decide whether to charge the storage or discharge the storage, and what rate to charge or discharge.

Although this Use Case is similar to the Request Real Power Use Case in its purpose, this Use Case uses broadcast pricing signals that are applicable to load, DER, as well as ES-DER, rather than explicit requests for specific increases or decreases of real power from specific ES-DER devices. These interactions between the utility DMS and the ES-DER are very loosely coupled.

The utility/ESP or the Customer EMS takes the following actions:

- Issue pricing signal (the actual form or content of the pricing signal will be established by the utility/ESP and is outside the scope of this specification):

  - Pricing signal

  - Requested ramp time for the ES-DER system to move from its current output to any new output (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual real power setpoint)

  - Rejected (plus reason: equipment not available, message error, overridden)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically or upon event | DMS | DER EMS | DMS broadcasts pricing signals for energy, without targeting ES-DER explicitly | Pricing signal | The pricing signal is applicable to loads, DER, and ES-DER. the actual form or content of the pricing signal is outside the scope of this Use Case |
| 2a | Upon receipt of pricing signal | DER EMS | ES-DER | DER EMS determines whether to respond and how “best” to respond to the pricing signal, including the increase or decrease in real power, and the ramp rate | Command to adjust real power at ramp rate | The DER EMS assesses the customer settings, its local situation, and other parameters to determine how it will respond to the pricing signal |
| 2b | Response to real power change request | ES-DER | DER EMS | Response to change real power command | Successful (plus actual real power value) Rejected (plus reason: equipment not available, message error, overridden) |  |

## Use Case: Adjust Power Factor

Narrative

The request to adjust the power factor of ES-DER devices can be determined only in conjunction with considering all other available corrective measures and their impacts on other operational parameters, such as capacitor banks on feeders. Therefore, additional information exchanges will take place between DMS and other actors before this request can be issued to the ES-DER. This broader analysis could introduce some additional time between the triggering event and the issuing of the Adjust Power Factor request to selected ES-DER.

Fixed power factor will be managed through issuing a power factor angle value. In addition, a ramp rate (angle versus time) and a delay time before starting will be included so that not all ES-DER systems change state abruptly or at the same time.

A timeout period is included for reverting to the default state of the ES-DER system, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

The utility/ESP or the DER EMS takes the following actions:

- (Optional) Request status of ES-DER system: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status.

- Issue command to adjust power factor setpoint:

  - Command to adjust the power factor angle

  - Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status, such as resetting the power factor setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual output power factor value)

  - Rejected (plus reason: equipment not available, message error, overridden)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to assess the alarm or event to determine if a power factor correction (or other) action is needed for selected ES-DER | Alarm/event information Appropriate SCADA information | The event may be that significant power system changes have occurred near the selected ES-DER, thus changing power system efficiency or reliability |
| 2a | Power factor correction is needed for selected ES-DER | DMS | DER EMS | Request status of ES-DER to determine whether they can change their power factor angle enough | Request for status and power factor measurement information | This step is optionally used in direct interactions, but cannot be used in broadcast/multicast interactions |
| 2b | Status request | DER EMS | ES-DER | Request status | Request for status and power factor measurement information |  |
| 2c | Response to status request | ES-DER | DER EMS | Response to status request | ES-DER status and power factor measurement information |  |
| 2d | Response to status request | DER EMS | DMS | Response to status request | ES-DER status and power factor measurement information |  |
| 3a | Power factor correction is needed for selected ES-DER | DMS | DER EMS | Request selected ES-DER to change their power angle | Request to adjust the power factor angle Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, Timeout period, after which the ES-DER system will revert to its default status, such as resetting the power factor setpoint to its default value | The three additional parameters are optional: If ramp rate not included, then use previously established default ramp rate If time window not included, then default time window for this function will be used If timeout not included, then default timeout period for this function will be used |
| 3b | Power factor change request | DER EMS | ES-DER | Command ES-DER to change power factor angle | Command to adjust power factor angle at requested rate | DER EMS can issue commands to ES-DER |
| 3c | Response to power factor change request | ES-DER | DER EMS | Response to change power factor angle command | Successful (plus actual output power factor value) Rejected (plus reason: equipment not available, message error, overridden) |  |
| 3d | Response to power factor change request | DER EMS | DMS | Response to change power factor angle command | Successful (plus actual output power factor value) Rejected (plus reason: equipment not available, message error, overridden) | Optional step – only if direct interactions are used. |

## Use Case: Volt/Var Optimization: Energy Conservation Mode

Narrative

The Normal Energy Conservation mode reflects the utility’s calculation of the most efficient and reliable var levels for ES-DER systems at specific distribution points of common coupling (PCC). This mode could also help compensate for local high voltage due to any ES-DER kW back flow on the circuit.

In this mode, ES-DER systems will be provided with a double array of setpoints: a set of voltage levels and their corresponding var levels. The voltage levels will range between V1 and V2 in increasing voltage values. Values between these setpoints will be interpolated to create at a piecewise linear volt/var function. The corresponding var levels would define the percent of Qmax (ranging between -100% and +100%) being requested for the voltage level.

Note: This mode may not always imply energy conservation in a more global sense, because PF=1 at one point may result in a higher than optimum voltage either at the same PCC and/or in other points of the distribution circuit.

The figure below is one example of volt/var settings for this mode. It is assumed that the var value between Vmin and V1 is the same as for V1 (Qmax in this example). The equivalent is true for the var value between V4 and Vmax (-Qmax in this example).

- Issue request to go into VVO Mode:

  - Request to go into VVO Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual output power factor value)

  - Rejected (plus reason: equipment not available, message error, overridden)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to assess the status of the power system to determine if changes to volt/var optimization is needed for selected ES-DER | Alarm/event/status information Appropriate SCADA measurements | The status may be that significant power system volt/var changes have occurred near the selected ES-DER, thus changing power system efficiency or reliability |
| 2a | Volt/var profile change is needed for selected ES-DER | DMS | DER EMS | Request status of ES-DER to determine whether they can change their volt/var profile enough | Request for status and volt/var measurement information | This step is optionally used in direct interactions, but cannot be used in broadcast/multicast interactions |
| 2b | Status request | DER EMS | ES-DER | Request status | Request for status and current volt/var information | Optional |
| 2c | Response to status request | ES-DER | DER EMS | Response to status request | ES-DER status current volt/var information |  |
| 2d | Response to status request | DER EMS | DMS | Response to status request | ES-DER status information | Only if Direct Interactions are established between DER EMS and DMS |
| 3a | Volt/var profile change is needed for selected ES-DER | DMS | DER EMS | DMS develops volt/var setpoints and issues volt/var arrays to selected ES-DER | Request VVO Mode Array of volt/var of setpoints Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately Timeout period, after which the ES-DER system will revert to its default status, such as resetting the maximum power setpoint to its default value | Optional parameters in the command: If volt/var array not included, then use previously established default array If ramp rate not included, then use previously established default ramp rate If time window not included, then default time window for this function will be used If timeout period not included, then default timeout period for this function will be used |
| 3b | VVO change request | DER EMS | ES-DER | Command ES-DER to change volt/var profile | Command to adjust volt/var profile at requested ramp rate (if previously constrained) |  |
| 3c | Response to VVO change request | ES-DER | DER EMS | Response to VVO command | Successful (plus actual real power value) Rejected (plus reason: equipment not available, message error, overridden) |  |
| 3d | Response to VVO change request | DER EMS | DMS | Response to change VVO command | Successful (plus actual output real power value) Rejected (plus reason: equipment not available, message error, overridden) | Optional step – only if Direct Interactions are used between the DER EMS and the DMS. |

## Use Case: Maximum Var Support Mode

Narrative

In this mode, ES-DER systems provide maximum vars currently available (Qmax available = 100%) without reducing kW output or exceeding Vmax. This mode would typically be invoked by the utility to support transmission var emergencies.

This function would essentially be represented as a straight horizontal line at Qmax = 100%, until the IEEE 1547 low voltage limit or ANSI C84.1 high voltage limit is reached or the inverter protective limits are hit (although the actual var value of Qmax itself could vary at different voltage levels).

The figure below provides one example of how a PV2 mode may be configured.   In this example, the inverter generates maximum capacitive vars for reduced voltages down to the cutoff limit Vmin.  As voltage increases above configuration point V1, var generation is ramped down, reaching zero at V2, so as not to drive the local system voltage too high.

The ramp rates and/or the randomized time-constant settings are also required.

- Issue request to go into Maximum Var Mode:

  - Request to go into Maximum Var Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the ES-DER system will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to assess the status of the power system to determine if maximum vars are needed for selected ES-DER | Alarm/event/status information Appropriate SCADA measurements | The status may be that significant power system volt/var changes have occurred near the selected ES-DER, thus changing power system efficiency or reliability |
| 2a | Maximum vars are needed from selected ES-DER | DMS | DER EMS | Request status of selected ES-DER to determine whether they can provide maximum vars | Request for status and var measurement information | This step is optionally used in direct interactions, but cannot be used in broadcast/multicast interactions |
| 2b | Status request | DER EMS | ES-DER | Request status | Request for status and current volt/var information | Optional |
| 2c | Response to status request | ES-DER | DER EMS | Response to status request | ES-DER status current volt/var information |  |
| 2d | Response to status request | DER EMS | DMS | Response to status request | ES-DER status and var information | Only if Direct Interactions are established between DER EMS and DMS |
| 3a | Maximum vars needed updated actions from ES-DER | DMS | DER EMS | DMS develops volt/var setpoints and issues volt/var arrays for maximum vars to selected ES-DER | Request Maximum Vars Mode Array of volt/var of setpoints Requested ramp time for the ES-DER system to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately Timeout period, after which the ES-DER system will revert to its default status, such as resetting the maximum power setpoint to its default value | Optional issues: If volt/var array not included, then use previously established default array If ramp rate not included, then use previously established default ramp rate If time window not included, then default time window for this function will be used If timeout period not included, then default timeout period for this function will be used |
| 3b | Maximum Vars request | DER EMS | ES-DER | Command ES-DER to go to Maximum Vars Mode | Command to go to Maximum Vars Mode at requested ramp rate (if previously constrained) |  |
| 3c | Response to Maximum Vars request | ES-DER | DER EMS | Response to Maximum Vars command | Successful (plus actual var value) Rejected (plus reason: equipment not available, message error, overridden) |  |
| 3d | Response to Maximum Vars request | DER EMS | DMS | Response to Maximum Vars command | Successful (plus actual var value) Rejected (plus reason: equipment not available, message error, overridden) | Optional step – only if Direct Interactions are used between the DER EMS and the DMS. |

## Use Case: Electric Vehicle Load Management

Narrative

The utility signals a load management level, such as request for improved efficiency or for flattening a peak power or for emergency scram.  The PEV participates in the event as required by the PEV program, such as stopping charging, slowing charging, or discharging. The PEV responses, or lack of responses, are captured for later billing and non-repudiation auditing purposes

Optimized Energy Transfer programs are designed to incentivize customers whom are willing to give the energy provider control over their load.  More specifically these programs allow energy providers to reduce or interrupt customer loads during critical grid events.  The idea is that the energy provider based on the grid event can actively manage the charging load by either reducing or interrupting it.  In either case, the active management will support turn off those who have higher state of charge while only reducing the charge rate of those that have lower state of charge.  Usually, the energy provider offers a vast array of options with programs varying in the quantity of events and length of reduction or interruption periods. These include Regulation Services and taking advantage of Spinning Reserves.

The Utility may offer the Customer an Optimized Energy Transfer Program. This offers the customer and utility an opportunity to take advantage of Regulation services and utilize Spinning reserves and other methods to match grid load to demand in a predictable and accountable aspect.

Regulation services, are used to continuously fine-tune the balance between power generation and demand, in terms of the voltage and the frequency of the grid. In many power markets, this function, called regulation or automatic generation control (AGC), is priced separately from power generation and procured as an ancillary service (another such service is spinning reserves). The grid operator needs to be able to ensure generators ramp output up or down in real time to meet customer reactive power needs, manage customer impact on system voltage, frequency and system losses and ensure that power-factor problems at one customer site do not affect power quality elsewhere in the system. Again, providing regulation services requires electricity generation capacity in excess of demand.

Spinning reserves refers to generating capacity that is up and running, and synchronized with the electricity grid (but not contributing power). Spinning reserves generators contribute to grid stability, helping to arrest the decay of system frequency when there is a sudden breakdown or loss of another generator. Again, typically, power plants that can provide fast response to the calls of the grid operator are the most suitable, e.g. gas turbines. The capacity required to provide spinning reserves can also be seen as an underutilized investment, although essential for managing market risks.

Steps

# Use Cases: Scheduled Real Power and Ancillary Services Commands

## Overview of Issuing Schedules for Real Power and Ancillary Services

Larger ES-DER systems and large aggregations of small ES-DER systems have significant influence on the distribution system and have local volt/var characteristics that may vary throughout the day.  As a result, a single volt/var configuration may not be suitable at all times. Sending many control commands may impact the communications system or may not be received in a timely manner, leading to inadequate ES-DER system responses. However, if schedules can be established that the ES-DER systems can follow autonomously, then these communication impacts can be minimized.

Therefore, in addition to direct control or broadcast/multicast requests, utilities and/or ESPs could send out “ES-DER Schedules” to individual and/or large groups of ES-DER systems, based on time, temperature, pricing signal, or possibly other criteria. This method allows more autonomous control with less tightly-coupled coordination, while requiring fewer interactions between the utility and the ES-DER.

For var support actions, ES-DER inverters could act in a similar manner to feeder capacitor banks, changing var settings based on a time schedule and/or temperature. This capability would most likely be used with larger installations of ES-DER inverters, for instance at a ES-DER farm, where the utility could manage the ES-DER inverters as part of primary feeder volt/var schemes.  The reason for this mode is that voltage sensed by these large inverters will differ from that sensed by nearby customers due to voltage drop on transformers and secondaries.  This is the same problem with voltage-switched capacitor banks.

## Actors for Scheduling

| Actor Name | Actor Type (person, organization, device, system, or subsystem) | Actor Description |
| --- | --- | --- |
| Distribution SCADA | System | DSCADA collects data from IEDs beyond the fence of the T&D substation and supports remote control of controllable devices in the field either in supervisory or close-loop modes. The field IEDs include utility DER and Micro-grid controllers, may include customer EMS. |
| DMS (Distribution Management System) | System | A set of integrated IT systems and ADA applications supporting the operations, maintenance, and planning of the electric distribution system |
| DER EMS | System | Energy management system, belonging to the owner or operator of the distributed energy resources (DER) Energy Storage - Distributed Energy Resource (ES-DER), that determines what actions to command the unit to perform. |
| Energy Storage - Distributed Energy Resource (ES-DER) | Device | Device that can store energy, and can be commanded to charge or discharge |
| ES-DER Schedule | Subsystem | Schedule of different ES-DER settings over time, temperature, pricing signal, or other criteria (e.g. voltage, frequency deviation, etc.) |

## Use Case: Scheduling for Real Power (Charge or Discharge ES-DER)

Narrative

This Use Case is the scheduled version of the “Request Real Power” function.  By sending a schedule to a device for charging and discharging, as opposed to immediate settings, the burden on the communication system may be reduced.  The settings for this function are still a percentage (based on system capacity), just as with the “Request Real Power” message.

These schedules can be  sent to DER EMS and/or ES-DER systems as follows:

During initialization of the interactions between the utility and the ES-DER, the utility or ESP issues one or more default ES-DER schedules (up to a limit of schedules determined during implementation). This allows subsequent commands to just be “Start schedule 1” or “Start schedule Peak Shave” without having to resend the schedule.

These ES-DER schedules can be updated as necessary over time.

These schedules consist of multi-column arrays of variable length (up to a maximum determined during implementation):

1st column: Value – Real power (percentage of nominal) at ECP

2nd column: Basis – time, temperature, pricing signal, or other criteria

3rd column: Range – range of time, temperature, pricing signal, or other criteria (range of time may be implicit, with the next “time” entry indicating the stop of the previous “time” entry)

4th column: Ramp – ramp rate to move from one real power setting to another

If Basis is time-based, the time will be relative to the start time of the schedule, which would be one of the parameters in the command from the utility/ESP.

The first time in the schedule would be 00:00, implying that the first value should be ramped to at the start time given in the “Start Schedule” command

The schedule can be stopped at its end or repeated: daily schedule, weekly schedule, etc.

If Basis is temperature-based, it is assumed the ES-DER has access to either local temperature or a broadcast temperature. Temperature ranges would need to be included in the schedule.

If Basis is pricing signal-based, it is assumed that a broadcast of the pricing signal will be provided. Depending upon the type of pricing signal, ranges may or may not need to be provided.

“Start Schedule” command: the request for the ES-DER to start a schedule includes:

Start schedule = xxx (identity of schedule)

Start time = yy:mm:dd, hh:mm:ss

Repeat/Do not repeat Schedule at yyy interval (e.g. daily)

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Upon initialization | DMS | DER EMS | Provide ES-DER Schedules for real power | ES-DER Schedule identifier Schedule arrays of 4 columns containing Value, Basis, Range, and Ramp | These schedules could be provided locally (e.g. downloaded from a laptop) rather than received over the utility communications network |
| 2 | Update existing ES-DER Schedules | DMS | DER EMS | Update ES-DER Schedules for real power | ES-DER Schedule identifier Schedule arrays of 4 columns containing Value, Basis, Range, and Ramp |  |
| 3 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to determine what schedule should be followed by selected ES-DER | Event information Appropriate SCADA information |  |
| 4a | Schedule is needed for selected ES-DER | DMS | DER EMS | Request that the identified schedule be followed | Start schedule = xxx (identity of schedule) Start time = yy:mm:dd, hh:mm:ss Repeat/Do not repeat schedule at yyy interval |  |
| 4b | ES-DER Schedule Basis changes (e.g. next time interval, changed temperature, new pricing signal) | DER EMS | ES-DER | Command ES-DER to change real power per schedule | Command to adjust real power (percentage of nominal) at requested ramp rate |  |
| 4c | Response to real power change request | ES-DER | DER EMS | Response to change real power command | Successful (plus actual real power value) Rejected (plus reason: equipment not available, message error, overridden) |  |

## Use Case: Scheduling Var Modes

Narrative

Schedules for Var Modes (Volt/Var Optimization and Maximum Vars) are more complex because the modes themselves are arrays of volt/var pairs. Therefore the 1st column Value would be the combination of the Mode and the identity of the volt/var array.

These schedules consist of multi-column arrays of variable length (up to a maximum determined during implementation):

1st column: Value – Volt/Var Mode and identity of volt/var array

2nd column: Basis – time, temperature, pricing signal, or other criteria

3rd column: Range – range of time, temperature, pricing signal, or other criteria (range of time may be implicit, with the next “time” entry indicating the stop of the previous “time” entry)

4th column: Ramp – ramp rate to move from one real power setting to another

Steps

| # | Triggering Event | Information Producer | Information Receiver | Description of Process/Activity | Information Exchanged | Notes or Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Upon initialization | DMS | DER EMS | Provide ES-DER Schedules for Var Modes | ES-DER Schedule identifier Schedule arrays of 4 columns containing Value, Basis, Range, and Ramp Arrays of volt/var pairs | These schedules could be provided locally (e.g. downloaded from a laptop) rather than received over the utility communications network |
| 2 | Update existing ES-DER Schedules | DMS | DER EMS | Update ES-DER Schedules for Var Modes | ES-DER Schedule identifier Schedule arrays of 4 columns containing Value, Basis, Range, and Ramp Arrays of volt/var pairs |  |
| 3 | Periodically or upon event | Distribution SCADA | DMS | Request for ADA applications to determine what schedule should be followed by selected ES-DER | Event information Appropriate SCADA information |  |
| 4a | Schedule is needed for selected ES-DER | DMS | DER EMS | Request that the identified schedule be followed | Start schedule = xxx (identity of schedule) Start time = yy:mm:dd, hh:mm:ss Repeat/Do not repeat schedule at yyy interval |  |
| 4b | ES-DER Schedule Basis changes (e.g. next time interval, changed temperature, new pricing signal) | DER EMS | ES-DER | Command ES-DER to change volt/var profile | Command to adjust volt/var profile at requested ramp rate (if previously constrained) |  |
| 4c | Response to volt/var change request | ES-DER | DER EMS | Response to change volt/var profile | Successful (plus actual volt/var values) Rejected (plus reason: equipment not available, message error, overridden) |  |

# Additional ES-DER Use Cases?

It is recognized that there could be many additional ES-DER Use Cases. For instance, there will be Plug-In Electric Vehicle (PEV) Use Cases where PEVs are being used at least partially as ES-DER rather than pure load. In addition, it is likely that ES-DER will be used for frequency stabilization, harmonic cancellation, black start, and many emergency functions. However, the list of Use Cases in this document represent a good start at identifying these interactions.