| Security Profile for Advanced Metering Infrastructure |  |
| --- | --- |
|  | Prepared for: The UtiliSec Working Group (UCAIug) & The NIST Cyber Security Coordination Task Group |  |
|  | Prepared by: The Advanced Security Acceleration Project (ASAP-SG) |  |
|  | Managed by: EnerNex Corporation 620 Mabry Hood Road Knoxville, TN 37923 USA (865) 218-4600 www.enernex.com |  |
|  | Version 0.46 September 18, 2009 |

Executive Summary

Table of Contents

1	Acknowledgements	1

2	Authors	2

3	Introduction	3

3.1	Purpose	4

3.2	Scope	4

3.3	Approach	4

3.4	Audience	5

3.5	Disclaimer/Status	5

4	Domain Analysis	6

4.1	Use case and scenario analysis	6

4.2	Logical architecture	9

4.3	Component definitions	13

4.3.1	AMI Communications Network Device	13

4.3.2	AMI Forecasting System	13

4.3.3	AMI Head End	13

4.3.4	AMI Meter	13

4.3.5	AMI Meter Management System	14

4.3.6	AMI Network Management System	14

4.3.7	Demand Response Analysis and Control System (DRAACS)	14

4.3.8	Field Tool/Device	14

4.3.9	Grid Control Center	14

4.3.10	Data Management System (MDMS)	14

4.3.11	Electric Meter	15

4.3.12	Party Meter/Submeter	15

4.4	AMI Security Service Domains	15

4.4.1	Delineation of Domains	15

4.4.2	Domain Characteristics	16

4.4.3	Domain Analysis – Significance, Relevance, and Influence	19

5	Recommended Controls	21

DHS-2.8 System and Communication Protection	21

DHS-2.8.1 System and Communication Protection Policy and Procedures	21

DHS-2.8.2 Management Port Partitioning	22

DHS-2.8.3 Security Function Isolation	23

DHS-2.8.4 Information Remnants	24

DHS-2.8.5 Denial-of-Service Protection	24

DHS-2.8.6 Resource Priority	25

DHS-2.8.7 Boundary Protection	25

DHS-2.8.8 Communication Integrity	26

DHS-2.8.9 Communication Confidentiality	27

DHS-2.8.10 Trusted Path	27

DHS-2.8.11 Cryptographic Key Establishment and Management	28

DHS-2.8.12 Use of Validated Cryptography	28

DHS-2.8.13 Collaborative Computing N/A	29

DHS-2.8.14 Transmission of Security Parameters	29

DHS-2.8.15 Public Key Infrastructure Certificates	30

DHS-2.8.16 Mobile Code	30

DHS-2.8.17 Voice-Over Internet Protocol	31

DHS-2.8.18 System Connections	31

DHS-2.8.19 Security Roles	32

DHS-2.8.20 Message Authenticity	32

DHS-2.8.21 Architecture and Provisioning for Name/Address Resolution Service	32

DHS-2.8.22 Secure Name / Address Resolution Service (Authoritative Source)	33

DHS-2.8.23 Secure Name/Address Resolution Service (Recursive or Caching Resolver)	34

ASAP-2.8.24 Secure Name/Address Resolution Service (Address Resolution Tampering)	34

DHS-2.9 Information and Document Management	35

DHS-2.9.1 Information and Document Management Policy and Procedures	35

DHS-2.9.2 Information and Document Retention	36

DHS-2.9.3 Information Handling	36

DHS-2.9.4 Information Classification	36

DHS-2.9.5 Information Exchange	37

DHS-2.9.6 Information and Document Classification	37

DHS-2.9.7 Information and Document Retrieval	38

DHS-2.9.8 Information and Document Destruction	38

DHS-2.9.9 Information and Document Management Review	39

DHS-2.9.10 Automated Marking	39

DHS-2.10 System Development and Maintenance	40

DHS-2.10.1 System Maintenance Policy and Procedures	40

DHS-2.10.2 Legacy System Upgrades	40

DHS-2.10.3 System Monitoring and Evaluation	41

DHS-2.10.4 Backup and Recovery	41

DHS-2.10.5 Unplanned System Maintenance	41

DHS-2.10.6 Periodic System Maintenance	42

ASAP-2.10.7 Field Tools	43

DHS-2.10.8 Maintenance Personnel	43

DHS-2.10.9 Remote Maintenance	44

DHS-2.12 Incident Response	44

DHS-2.12.1 Incident Response Policy and Procedures	44

DHS-2.12.2 Continuity of Operations Plan	45

DHS-2.12.3 Continuity of Operations Roles and Responsibilities	45

DHS-2.12.4 Incident Response Training	45

DHS-2.12.5 Continuity of Operations Plan Testing	46

DHS-2.12.5.3 Requirement Enhancements:	46

DHS-2.12.6 Continuity of Operations Plan Update	46

DHS-2.12.7 Incident Handling	47

DHS-2.12.8 Incident Monitoring	47

DHS-2.12.9 Incident Reporting	48

DHS-2.12.10 Incident Response Assistance	48

DHS-2.12.11 Incident Response Investigation and Analysis	49

DHS-2.12.12 Corrective Action	49

DHS-2.12.13 Alternate Data Storage Sites	50

DHS-2.12.14 Alternate Command/Control Methods	50

DHS-2.12.15 Alternate Control Center	51

ASAP-2.12.16 Business Data Backup	51

DHS-2.12.17 Control System Recovery and Reconstitution	52

DHS-2.12.18 Fail-Safe Response	52

DHS-2.14 System and Information Integrity	53

DHS-2.14.1 System and Information Integrity Policy and Procedures	53

DHS-2.14.2 Flaw Remediation	54

DHS-2.14.3 Malicious Code Protection	54

DHS-2.14.4 System Monitoring Tools and Techniques	57

DHS-2.14.5 Security Alerts and Advisories	58

DHS-2.14.6 Security Functionality Verification	58

DHS-2.14.7 Software and Information Integrity	59

DHS-2.14.8 Spam Protection	60

DHS-2.14.9 Information Input Restrictions	60

DHS-2.14.10 Information Input Accuracy, Completeness, Validity, and Authenticity	61

DHS-2.14.11 Error Handling	61

DHS-2.14.12 Information Output Handling and Retention	62

DHS-2.15 Access Control	62

DHS-2.15.1 Access Control Policy and Procedures	63

DHS-2.15.2 Identification and Authentication Policy and Procedures	64

DHS-2.15.3 Account Management	64

DHS-2.15.4 Identifier Management	65

DHS-2.15.5 Authenticator Management	66

DHS-2.15.6 Supervision and Review	67

DHS-2.15.7 Access Enforcement	68

DHS-2.15.8 Separation of Duties	69

DHS-2.15.9 Least Privilege	70

DHS-2.15.10 User Identification and Authentication	70

DHS-2.15.11 Permitted Actions without Identification or Authentication	71

DHS-2.15.12 Device Identification and Authentication	71

DHS-2.15.13 Authenticator Feedback	71

DHS-2.15.14 Cryptographic Module Authentication	72

DHS-2.15.15 Information Flow Enforcement	72

DHS-2.15.16 Passwords	73

DHS-2.15.17 System Use Notification	74

DHS-2.15.18 Concurrent Session Control	75

DHS-2.15.19 Previous Logon Notification	75

DHS-2.15.20 Unsuccessful Login Attempts	76

DHS-2.15.21 Session Lock	76

DHS-2.15.22 Remote Session Termination	77

DHS-2.15.23 Remote Access Policy and Procedures	77

DHS-2.15.24 Remote Access	78

DHS-2.15.25 Access Control for Portable and Mobile Devices	79

DHS-2.15.26 Wireless Access Restrictions	79

DHS-2.15.27 Personally Owned Information	80

DHS-2.15.28 External Access Protections	81

DHS-2.15.29 Use of External Information Control Systems	81

ASAP-2.15.30 Unauthorized Access Reporting	82

ASAP-2.15.31 Unauthorized Access	83

2.16 Audit and Accountability	83

DHS-2.16.1 Audit and Accountability Policy and Procedures	83

DHS-2.16.2 Auditable Events	84

DHS-2.16.3 Content of Audit Records	85

DHS-2.16.4 Audit Storage Capacity	86

DHS-2.16.5 Response to Audit Processing Failures	86

DHS-2.16.6 Audit Monitoring, Analysis, and Reporting	87

DHS-2.16.7 Audit Reduction and Report Generation	87

DHS-2.16.8 Time Stamps	87

DHS-2.16.9 Protection of Audit Information	88

DHS-2.16.10 Audit Record Retention	88

DHS-2.16.11 Conduct and Frequency of Audits	88

DHS-2.16.12 Auditor Qualification	89

ASAP-2.16.13 Audit Tools	90

DHS-2.16.14 Security Policy Compliance	90

# Acknowledgements

UtiliSec Working Group (WG) and AMI-SEC Task Force (TF) would like to acknowledge the work of the primary authors, contributing authors, editors, reviewers, and supporting organizations. Specifically, we would like to thank:

- ASAP-SG (Advanced Security Acceleration Project – Smart Grid)

  - The Security Team including resources from Consumers Energy, EnerNex Corporation, InGuardians, the Software Engineering Institute at Carnegie Mellon University, Oak Ridge National Laboratory, and Southern California Edison

  - Supporting organizations including The United States Department of Energy

  - Participating utilities, including…

- The utilities, vendors, consultants, national laboratories, higher education institutions, governmental entities, and other organizations that have actively contributed to and participated in the activities of the UtiliSec WG and AMI-SEC Task Force

The UtiliSec WG and AMI-SEC TF would also like to thank the Department of Homeland Security (DHS) Cyber Security Division, National Institute of Standards and Technology (NIST) Computer Security Division, North American Reliability Corporation (NERC) and The Common Criteria for the works that they have produced that served as reference material for the AMI Systems Security Requirements document.

# Authors

Len Bass

Bobby Brown

Kevin Brown

Matthew Carpenter

James Ivers

Teja Kuruganti

Howard Lipson

Jim Nutaro

Justin Searle

Vishant Shah

Brian Smith

James Stevens

Edited by: Darren Highfill

# Introduction

The Advanced Metering Infrastructure Security (AMI-SEC) Task Force was established August 2007 under the Utility Communications Architecture International Users Group (UCAIug) to develop consistent security guidelines for the initial AMI portion of the Smart Grid. The Task Force set forth an aggressive schedule for 2008, with voluntary resources and found this was not sufficient to maintain the desired pace; therefore, several utilities expressed the need for further and faster assistance with AMI security. In response, the AMI-SEC leadership defined a project to accelerate and augment the work of the Task Force, referred to as ASAP.

The Advanced Security Acceleration Project Smart Grid (ASAP-SG) has evolved to a collaborative effort between EnerNex Corporation, multiple major North American utilities, the National Institute of Standards and Technology, and the United States Department of Energy (DOE), including resources from Oak Ridge National Laboratory and the Software Engineering Institute of Carnegie Mellon University. The Electric Power Research Institute (EPRI) played a major role in bringing their utility membership to the original ASAP project and they may do so again with ASAP-SG.

Now with the objectives defined in the American Reinvestment and Recovery Act of 2009, utilities are under greater pressure to aggressively deploy smart grid technologies and applications. Additionally the President of the United States, U.S. Congress, the Federal Energy Regulatory Commission, the DOE, and numerous other authoritative entities have identified cyber security for the smart grid as a top priority. This project addresses both the recommendation by the utilities of the Open Smart Grid Committee and government entities to take the next step to produce actionable, understandable, and targeted guidance for securing the smart grid.

## Purpose

The purpose of this document is to present security concerns relevant to AMI and provide guidance and security controls to organizations developing or implementing AMI solutions for the Smart Grid. The intent of the document is to provide prescriptive, actionable guidance for how to build-in and implement security for AMI smart grid functionality. This document provides a tailored security profile based on AMI use cases. For ease of management, functions and components are first aggregated into security domains. The specification is neutral to vendor specific implementations and architectures.

## Scope

The intent of this document is provide normative security guidance for AMI systems from the meter data management system (MDMS) up to and including the HAN interface of the smart meter. The controls selected and adapted to AMI in this document are limited to the components and interfaces that have the primary purpose of supporting AMI. Architecturally the scope represents the components and communications from the MDMS and its related components to the smart meter. This document does not cover organizational security controls that are superfluous to the organization.

Informative security guidance may be provided for AMI related components that extend beyond the external interfaces of the MDMS and smart meter.

## Approach

The ASAP-SG team took the following steps to develop recommended cyber security controls for AMI. This document also explains the process for examining risk and cyber security concerns within the electric power industry.

- Examination of AMI Use Cases

- Evaluation of risk for AMI

- AMI security service domain analysis

- Modification and enhancement of DHS controls

Many AMI systems share commonality at the logical level, although systems will vary among utilities based on technology choices and features they intend to support. Publicly available material was used and reviewed as a reference to the logical structure of AMI systems. The primary source used for UML use cases, scenarios and sequence diagrams was www.smartgridipedia.org. From this analysis, the ASAP-SG team extracted a logical architecture and examined the communications among logical and physical components.

The ASAP-SG team evaluated the risks associated with AMI components and interfaces. Where necessary, components were decomposed into sub-components where application of security controls differ and are further elaborated later in this document. Cyber security concerns surrounding current AMI components and technology were taken in consideration such as key management, firmware assurance and protection, and trust between intra- and inter-organizational users and objects.

Security controls were selected based on applicability to components and messages of AMI scenarios that were studied. Security service domains were used as a tool to further characterize these components with respect to additional security considerations. The assigning of components to AMI security service domains, examination of processes, communication and security considerations were used in the selection of requirements for each component.

## Audience

The primary audience of this document is for organizations that are developing or implementing AMI solutions. This document is written at the normal level of utility security experience for system owners, system implementers and security engineers. The user is assumed to be experienced at information asset risk estimation. The user is further assumed to be knowledgeable in developing security requirements and guidance.

## Disclaimer/Status

Please note that the recommended controls listed in this document are adaptations of the DHS controls as appropriate for AMI security. The DHS control section numbers are only provided for traceability, and not intended to indicate that the controls in this document are the DHS controls themselves. When the ASAP-SG team created controls for which there was no DHS counterpart, the "ASAP-" prefix is used instead of "DHS-".

# Domain Analysis

Security requirements were selected based on the domain analysis described in this section. While AMI systems will vary among utilities, based on technology choices and features they intend to support, much is common at the logical level. A good summary of features and logical structure can be found in publicly available and reviewed material.

We began our analysis with a review of use cases and related detailed scenarios provided by the AMI Enterprise community (based on work contributed to the community by SCE). This analysis is discussed in section 2.1.

From this analysis, we extracted a logical architecture (presented in section 2.2) summarizing the communications among logical components. These logical components are further elaborated in section 2.3.

Finally, we used security domains (described in section 2.4) to further characterize these components with respect to additional security considerations. This aggregate understanding of the AMI domain, the components within the domain, and their patterns of communication and security considerations were used in the selection of requirements for each logical component.

## Use case and scenario analysis

Several collections of use cases have been developed by the community, but we decided to work from the AMI Enterprise use cases documented on SmartGridiPedia. This decision was driven by the following criteria

- rich information content (in the form of a collection of detailed scenarios for each use case)

- good coverage of AMI features

- community review of the use cases and scenarios, reflecting some degree of community consensus in the AMI space

- public availability

Given the scope of this security profile, we restricted our attention to those use cases describing AMI features and business flows. Specifically, these are scenarios B1-B4, Consolidate Demand Response and Load Control, C1-C4, D4, I1-I3, and S1.

This set of scenarios is not, however, assumed to be complete. Other AMI features or alternate business flows are likely. From the available material, however, we were able to extract a great deal of information for how typical components of an AMI system interact, what types of information or control signals flow between components, and which components are isolated from each other.

Figure 1: A UML activity diagram for Scenario 2 of use case B2

Figure 1 shows one of the scenarios as an example. From diagrams of this kind, we extracted

- Components: each swimlane depicts a different entity involved in the business flow captured in the scenario's activity diagram. Some components represent system components, while others represent human actors. For our purposes, we restricted our attention to system components. Additionally, some components were deemed outside the scope of the AMI profile.

- Communication: arrows between nodes often represent some communication of information or control signals between components. Other times, arrows simply represent the sequence of activities. Some interpretation was necessary. The key information extracted at this point was the nature of information and control exchanged between components.

Some inconsistencies and oversights were encountered in analyzing the use cases and scenarios. For example, in scenario 9 of use case B1, a meter is shown communicating with the MDMS without going through a Head End. This was inconsistent with many other scenarios, and assumed to be an oversight. Such corrections were made in several places to arrive at a consistent logical architecture.

## Logical architecture

A logical architectural view depicts logical components and their interactions. By logical components, we refer to conceptual elements defined by common functionality. A logical architectural view does not attempt to capture deployment information, such as allocation of functionality to hosts or network segments. Nor does it attempt to capture all terminology and physical configurations represented by different products.

The logical architectural components have only the meaning defined in this document, regardless of how some other party may define the same terms.

As such, any product implementing the function of a logical component, shall satisfy all security requirements identified in Section 3 that apply to that component—regardless of whether the product uses that component's name or whether it implements the functions of multiple components. Products that implement the functions of multiple components shall satisfy all security requirements of each component whose functions it implements.

This view was extracted from the use cases and scenarios described in Section 2.1, with some simplifications. In these figures, we spotlight the communications between components that are in-scope for the AMI profile and between in-scope components and out-of-scope components. We omit all communications between out-of-scope components. For example, while the source material describes the nature of some communications between an Enterprise Asset Management component and a Workforce Management System, this information omitted to allow focus on the components that are in the scope of this profile. Likewise, we did include information on interactions between human actors.

Figure 2: AMI Logical Architectural View (Internal Perspective)

Figure 2 shows a draft of the resulting logical architecture. This presentation of the view focuses on interactions between components that are in-scope for this profile. Each point of interaction between components is represented by a numbered line. Dashed lines represent interactions between in-scope components and out-of-scope components or actors. Table 1 summarizes the communications between in-scope components; each summary presents a variety of communications and commands communicated between the components without attempting to be complete.

| Line # | Direction | Summary of communication |
| --- | --- | --- |
| 1 | to AMI Meter | Meter read requests, turn on/off commands, pricing data, provisioning requests, firmware updates, prepayment information |
|  | to AMI Head End | Meter read data, various meter events (e.g., tampering, outage, and restoration), various confirmations (e.g., meter turn on/off, load shed start/end, and meter provisioning), HAN communication, error logs |
| 2 | to MDMS | Meter read data, various meter events and confirmations, HAN equipment responses, outage and restoration notifications, event logs |
|  | to AMI Head End | Meter read requests, load shed commands, planned outage information, HAN equipment commands |
| 6 | to AMI Head End | Meter read data |
|  | to Third Party Meter/Submeter | Meter read requests |
| 9 | to Field Tool/Device | Stored meter data (including meter read data and ID) and logs, turn on/off confirmation, AMI system registration success, meter test results |
|  | to AMI Meter | Request for all meter data and logs, credentials for field person using Field Tool/Device, turn on/off commands, meter configuration data, request communication test and self-test results |
| 10 | to MDMS | Stored meter data |
|  | to Field Tool/Device | None identified |
| 11 | to AMI Meter Management System | Problem meters report, meter service order request, meter read data |
|  | to MDMS | Meter read requests, closed meter order status |
| 18 | to AMI Meter Management System | Various meter events (e.g., intrusion, inversion, and customer load detected), meter status, meter location change or network disconnection, meter service order request, confirmation of firmware update download |
|  | to AMI Head End | Non-electric meter read requests, meter reconfiguration, updated firmware, command to execute firmware update, HAN device ping requests |
| 21 | to AMI Network Management System | Meter events, activity records |
|  | to AMI Head End | Non-electric meter read requests |
| 22 | to AMI Head End | Meter read data, establish connection confirmation, non-electric meter events |
|  | to Non Electric Meter | Meter read requests, establish connection commands, meter event monitoring requests |
| 24 | to MDMS | Load shed control notification |
|  | to DRAACS | Load shed event end |
| 25 | to DRAACS | Load control request |
|  | to Grid Control Center | Load shed report |
| 37 | to AMI Head End | Power outage and restoration notifications, meter last gasp messages, collector running on battery messages, collector power restored messages |
|  | to AMI Communications Network Device | None identified |
| 39 | to AMI Communications Network Device | Meter last gasp messages |
|  | to AMI Meter | None identified |
| 49 | to AMI Meter Management System | Meter inventory requests |
|  | to AMI Forecasting System | Meter inventory responses |

Table 1: Summary of Communication in AMI Logical Architectural View (Internal Perspective)

Figure 3: AMI Logical Architectural View (Full Perspective)

Figure 3 shows an expansion of this view in which out-of-scope components and actors are included (each dashed line is replaced by one or more numbered line). Interactions between out-of-scope components and actors are not shown.

There are several remaining issues to be resolved in ongoing validation activities, such as

- Can any meter communication go directly to the AMI Head End, or must all communication be routed via the AMI Communications Network Device? Note that these questions apply to all three varieties of meters in the diagram.

- What is the distinction between the AMI Meter Management System and the AMI Network Management System? Have these been consistently separated?

## Component definitions

The following sections provide functional definitions of the logical components used in this document.

### AMI Communications Network Device

The AMI Communications Network device relays, routes, aggregates, or otherwise enables and facilitates communication between AMI components in the field and the utility operations center. This component carries all information exchanged by the operations center and field devices.

### AMI Forecasting System

The AMI Forecasting System tracks the number of meters available for deployment and maps the inventory to anticipated deployment schedule. It maintains an appropriate level of meter inventory.

### AMI Head End

The AMI Head End is responsible for two-way communications with AMI Meters to retrieve data and execute commands. It balances load on the communications network resulting from scheduled meter reads. It retries meters during communications failures and monitors the health of the advanced metering infrastructure. It also remotely manages and implements firmware updates, configuration changes, provisioning functions, control and diagnostics.

### AMI Meter

An AMI Meter is an advanced electric revenue meter capable of two-way communications with the utility. It serves as a gateway between the utility, customer site, and customer’s HAN devices and/or load controllers. It measures, records, displays, and transmits data such as energy usage, generation, text messages, and event logs to authorized systems. It may optionally include a disconnect switch that can be used to remotely provide or disconnect service.

AMI Meters are deployed on devices located in the field (e.g., on the side of a customer's home), and as such have limited physical protection.

### AMI Meter Management System

An AMI Meter Management System acts as a global data repository for information about each AMI Meter. It tracks deployment and operational status of meters. It also provides firmware updates for meters. An AMI Meter Management System is supply chain centered as opposed to the MDMS, which is focused on metrology (usage) data.

### AMI Network Management System

An AMI Network Management System acts as a global data repository for information about each AMI communication device, configurations of individual devices, and configuration of the network as a whole. It also tracks operational status of AMI communications.

### Demand Response Analysis and Control System (DRAACS)

A DRAACS sends demand response event notifications to meters and load control devices through the AMI system. It provides demand response options to operators, market traders, etc. based on predefined groupings of customers and statistical analysis of how those customers have responded in the past.

### Field Tool/Device

Field tools and devices are portable computing systems used by field personnel to connect to components in the field to perform maintenance, upgrades, diagnostics, and similar activities. It has a wireless connection to utility systems, which communicates information utility field personnel may need to perform installations or other service.

### Grid Control Center

A Grid Control Center component comprises the utility’s operations centers; real-time data and software applications used by those centers (e.g., EMS and SCADA); displays used to facilitate decision making; and applications outside of the operations center that interact with applications used for grid control.

### Data Management System (MDMS)

An MDMS aggregates, validates, estimates and permits editing of meter data such as energy usage, generation, and meter logs. An MDMS stores this data for a limited amount of time before it goes to a data warehouse and makes this data available to authorized systems.

### Electric Meter

Non-electric Meters are components used for metering non-electric services (e.g., gas and water meters). Non-electric Meters sometimes use AMI networking infrastructure to provide information back to non-electric utilities. Like AMI Meters, Non-electric Meters are deployed in the field, and as such have limited physical protection.

### Party Meter/Submeter

A Third Party Meter/Submeter is a metrology device that allows for the monitoring of usage on a portion of a distribution network past (at a finer granularity) a main meter. A submeter may not be owned by the utility. Third Party Meters/Submeters are deployed in the field, and as such have limited physical protection.

## AMI Security Service Domains

We built much of our analysis off the work performed by the AMI-SEC Task Force in 2008, especially with regard to security domains – a concept introduced to the electric power sector by the IntelliGrid Architecture Project in 2003. A security domain is an area within which one may assume a relatively consistent set of constraints and expectations with respect to security. Security domains are thereby used as a tool for analyzing devices, applications, and components for characteristics that would beg specific control requirements. However, a thorough comprehension of the security domain concept as an analysis tool is not essential to the application of the control recommendations, nor is an understanding the security domains presented herein. We used security domains as one tool among several to inform our decisions about recommended controls, and offer these comments as insight into our selection of recommendations.

### Delineation of Domains

The 2009 AMI Security Service Domains diagram is very similar to the original drawing from the AMI System Security Requirements with one formatting change and one technical change. The drawing has been rotated 90 degrees counter-clockwise to facilitate easier reading, and the Utility Enterprise domain now extends to interface directly with the Managed Network domain.

Figure 4: AMI Security Service Domains

Each of the AMI Security Service Domains represents a comprehensive set of concerns including (but not limited to) ownership, control, physical access, logical access, information sensitivity, and business functionality. Physical assets are distributed throughout the drawing and are not presumed to move or change domain. Information flows across the drawing, passing from one domain to another by crossing the boundaries between domains and is not presumed to “jump” a domain in its path.

The drawing assumes other utility enterprise applications beyond AMI such as Outage Management and Customer Information will connect through the Utility Enterprise domain. Field applications such as the Home Area Network or other utility meters (i.e., gas or water) will connect through the Premise Edge or Utility Edge domain, respectively, as discussed below.

### Domain Characteristics

While a thorough examination of each AMI Security Service Domain provides the security analyst with a strong tool for evaluation of controls, such a discussion is not captured herein and is not essential to implementation of these recommendations. We do, however provide a brief description for each of the AMI Security Service Domains below. In essence, the questions the AMI Security Service Domains are trying to address are:

- Where does it reside in terms of utility facilities and physical environmental controls?

- Who owns it?

- Who is responsible for operating it?

- With what (types of) systems does it interface?

The AMI Security Service Domains also serve as a mechanism by which to level security requirements across multiple logical components. This is done in the interest of preventing “hop scotching” from an insignificant component (e.g., a print server) to a significant component (e.g., customer database). We endeavored to treat all components within a security domain equally to the extent practical or applicable for the component. The NERC CIP standards employ a similar concept with Critical Cyber Assets and Cyber Assets within the same Electronic Security Perimeter.

We have also included some questions to help the analyst determine whether a component falls into a given domain. In examining these questions, we used the following rules:

- A component should satisfy all the questions posed for a particular domain.

- If a component satisfies all questions for more than one domain, the component should be decomposed further until each sub-component maps to one and only one domain.

- If a component does not satisfy all the requirements of any domain, something is wrong and we need to either:

  - re-examine the asset

  - re-examine our delineation of domains

  - determine the component is out-of-scope

Using this approach, we were able to clarify our understanding of each component and several key characteristics that influenced subsequent control selection.

| Security Domain | Description | Criteria | Examples (AMI) |
| --- | --- | --- | --- |
| Utility Enterprise | Processing and/or storage of business application data, and support of utility enterprise applications | Is the asset centrally located (vs. field deployed and distributed)? (Y) | Meter Data Management System (MDMS), Customer Information System (CIS) |
|  |  | Does the asset control business operation (i.e., not communications behavior) of assets or provide business processing of data from assets in the Utility Edge domain? (Y) |  |
|  |  | Does the asset interface with utility enterprise applications (or their assets)? (Y) |  |
| Automated Network | Collection, transmission, translation, staging, and associated transformation of field communications | Is the asset centrally located (vs. field deployed and distributed)? (Y) | AMI Head End, AMI Network Management System |
|  |  | Does the asset provide an interface for assets in the Utility Enterprise domain to access assets in the Utility Edge or Premise Edge domains? (Y) |  |
|  |  | Does the asset provide a singular logical point of interface to assets in the Utility Enterprise domain for business data from assets in the Utility Edge or Premise Edge domains? (Y) |  |
| Managed Network | Oversight, administration, and control of Automated Services and Communication Services | Does the asset provide an interface for monitoring or manipulation of functions performed by assets in the Automated Network or Communications domains? (Y) | Management Console |
| Communications | Relaying, routing, and aggregation of field communications | Is the asset field deployed? (Y) | Field Area Network (FAN), Backhaul |
|  |  | Is the asset part of the communications mechanism connecting centralized utility applications with distributed, field deployed assets? (Y) |  |
| Utility Edge | Support of field deployed utility equipment and devices (i.e., monitoring, measurement, and/or control) | Is the asset field deployed? (Y) | Metrology, Disconnect Switch |
|  |  | Is the asset owned and operated by the utility? (Y) |  |
|  |  | Does the asset perform a function critical or essential to the operations or business of the utility? (Y) |  |
| Premise Edge | Support of customer equipment and devices (i.e., provisioning, monitoring, measurement, and/or control) | Is the asset field deployed? (Y) | Home Area Network (HAN) Interface |
|  |  | Does the asset provide an interface for the customer (or their assets)? (Y) |  |

Table 2: AMI Security Service Domain Characteristics

It is important to note that the AMI Security Service Domains form logical points of demarcation with regards to the system. Many commonly found devices and applications in AMI systems (and sometimes components whose functions they implement) actually span two or more domains. Where this occurred, we decomposed the component further into discrete sub-components until each sub-component could fit into one and only one domain. Recommended controls may be associated with logical components or sub-components. Further work will drive recommendations in some areas to increased levels of detail and prescription and may refine allocation of controls from components to sub-components.

One particular example of interest is the AMI Meter, which as a whole would span the Communications, Utility Edge, and Premise Edge domains. We therefore decomposed this component into the metrology and disconnect switch (if present) in the Utility Edge domain, the Field Area Network interface in the Communications domain, and the Home Area Network interface in the Premise Edge domain. Each of these sub-components and therefore any product implementing their function shall satisfy all security requirements identified in Section 3 that apply to that sub-component. The end result is that an AMI Meter inherits security requirements derived from the characteristics and constraints of the Communications, Utility Edge, and Premise Edge domains.

### Domain Analysis – Significance, Relevance, and Influence

The AMI Security Service Domain analysis does not produce any directly actionable guidance contained in this document. Instead, the analysis proved to be a strong tool for driving convergence of understanding regarding security constraints and expectations of the logical components identified. By examining these components in light of multiple security characteristics simultaneously (as guided by the AMI Security Service Domains), we were able to discern where components should be decomposed into sub-components, differentiate needs according to their most relevant attributes, and better defend selection of controls.

# Recommended Controls

The following controls are adapted from the DHS Catalog of Control Systems Security and have been modified or extended as appropriate for AMI security. The DHS control section numbers are only provided for traceability, and not intended to indicate that the controls in this document are the DHS controls themselves. When the ASAP-SG team created controls for which there was no DHS counterpart, the "ASAP-" prefix is used instead of "DHS-".

DHS-2.8 System and Communication Protection

System and communication protection consists of steps taken to protect the AMI components and the communication links between system components from cyber intrusions. Although AMI system and communication protection might logically include both physical and cyber protection, this section addresses only cyber protection. Physical protection is addressed in Section 2.4 of the DHS controls.

DHS-2.8.1 System and Communication Protection Policy and Procedures

DHS-2.8.1.1 Requirement:

The organization shall develop, disseminate, and periodically review and update:

- A formal, documented system and communication protection policy that addresses:

  - The purpose of the AMI system and communication protection policy as it relates to protecting the organization’s personnel and assets;

  - The scope of the AMI system and communication protection policy as it applies to all the organizational staff and third-party contractors;

  - The roles, responsibilities and management accountability structure of the security program to ensure compliance with the organization’s system and communications protection policy and other regulatory commitments;

- Formal, documented procedures to facilitate the implementation of the AMI system and communication protection policy and associated systems and communication protection controls.

DHS-2.8.1.2 Supplemental Guidance:

The organization shall ensure the AMI system and communication protection policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance.  The AMI system and communication protection policy needs to be included as part of the general information security policy for the organization. System and communication protection procedures can be developed for the security program in general and an AMI system in particular, when required.

These documents also need to include a documented plan that covers the policies and procedures that cover a breach in security.

DHS-2.8.1.3 Requirement Enhancements:

None.

DHS-2.8.2 Management Port Partitioning

DHS-2.8.2.1 Requirement:

AMI components must separate telemetry/data acquisition services from management port functionality.

DHS-2.8.2.2 Supplemental Guidance:

The AMI system management port needs to be physically or logically separated from telemetry/data acquisition services and information storage and management services (e.g., database management) of the system. Separation may be accomplished by using different computers, different central processing units, different instances of the operating systems, different network addresses or protocol ports (e.g., TCP ports), combinations of these methods, or other methods as appropriate.  Such precautions reduce the risk of allowing access to a data acquisition server and can help limit the damage of a compromised system.

Configuration and testing ports for AMI components should be disabled when not in use. 
Depending on the criticality of the system it may be advised that a device be physically disconnected.

DHS-2.8.2.3 Requirement Enhancements:

None.

DHS-2.8.3 Security Function Isolation

DHS-2.8.3.1 Requirement:

AMI components must isolate security functions from non-security functions.

DHS-2.8.3.2 Supplemental Guidance:

AMI components must isolate security functions from non-security functions by means of partitions, domains, etc., including control of access to and integrity of the hardware, software, and firmware that perform those functions. The AMI system maintains a separate execution domain (e.g., address space) for each executing process. Some AMI components may not implement this capability. In situations where it is not implemented, the organization details its risk acceptance and mitigation in the AMI system security plan

The AMI system must employ the following underlying hardware separation mechanisms to facilitate security function isolation:

- Each AMI component isolates critical security functions (i.e., functions enforcing access and information flow control) from both non-security functions and from other security functions;

- Each AMI component minimizes the number of non – security functions included within the isolation boundary containing security functions;

- AMI security functions are implemented as largely independent modules that avoid unnecessary interactions between modules;

- In each AMI component, security functions are implemented as a layered structure minimizing interactions between layers of the design and avoiding any dependence by lower layers on the functionality or correctness of higher layers.

- Passwords and/or security keys should be of limited value, avoiding significant reuse of keys or passwords between different components and users. For example, compromising one key must not allow compromise of an entire network.

DHS-2.8.3.3 Requirement Enhancements:

None.

DHS-2.8.4 Information Remnants

DHS-2.8.4.1 Requirement:

AMI components shall prevent unauthorized or unintended information transfer via shared system resources.

DHS-2.8.4.2 Supplemental Guidance:

Control of information system remnants, sometimes referred to as object reuse, or data remnants, must prevent information, including cryptographically protected representations of information previously produced by the AMI system, from being available to any current user/role/process that obtains access to a shared system resource (e.g., registers, main memory, secondary storage) after that resource has been released back to the information system.  Such information must be cleared before freeing the resource for other use.

DHS-2.8.4.3 Requirement Enhancements:

None.

DHS-2.8.5 Denial-of-Service Protection

DHS-2.8.5.1 Requirement:

AMI components shall protect against or limit the effects of denial-of-service attacks.

DHS-2.8.5.2 Supplemental Guidance:

A variety of technologies exist to limit, or in some cases, eliminate the effects of denial-of-service attacks. For example, network perimeter devices can filter certain types of packets to protect devices on an organization’s internal network from being directly affected by denial-of-service attacks.

- The AMI system must restrict the ability of users to launch denial-of-service attacks against other AMI components or networks.

- The AMI system must manage excess capacity, bandwidth, or other redundancy to limit the effects of information flooding types of denial-of-service attacks.

- Wireless assets and networks are also vulnerable to radio-frequency jamming and steps must be taken and personnel trained to address tracking and resolution of such issues. This may include radio-frequency direction finding and other such technologies.

DHS-2.8.5.3 Requirement Enhancements:

None.

DHS-2.8.6 Resource Priority

DHS-2.8.6.1 Requirement:

AMI components must limit the use of resources by priority.

DHS-2.8.6.2 Supplemental Guidance:

Priority protection helps prevent a lower-priority process from delaying or interfering with the AMI system servicing any higher-priority process.

DHS-2.8.6.3 Requirement Enhancements:

None.

DHS-2.8.7 Boundary Protection

DHS-2.8.7.1 Requirement:

The organization shall define the external boundary(ies) of the AMI system. Procedural and policy security functions must define the operational system boundary, the strength required of the boundary, and the respective barriers to unauthorized access and control of system assets and components. The AMI system monitors and manages communications at the operational system boundary and at key internal boundaries within the system.  In AMI, the very concept of boundaries is problematic.   Internal systems within the organization may be more easily protected than components which reside outside significant physical boundaries and controls.  Meters and poll-top and other systems without significant controls and external monitoring cannot be amply secured and should always be considered relatively untrusted.

DHS-2.8.7.2 Supplemental Guidance:

Any connection to the Internet or other external network or computer system needs to occur through managed interfaces (e.g., proxies, gateways, routers, firewalls, guards, encrypted tunnels). AMI system boundary protections at any designated alternate processing/control sites must provide the same levels of protection as that of the primary site.

At this time components and systems connected to the Internet constitute a substantial increase in risk for the core functionality of the AMI system. Connections to the Internet and other public networks are discouraged for AMI systems.

The HAN is not controlled or owned by the utility, and should be treated as a hostile network by the AMI meter.  Because of this, we recommend that AMI components should not request or accept information from HAN components.  We recommend that AMI components should only push traffic to the home area network.

The following guidance also applies:

- The organization physically must locate publicly accessible AMI system components to separate sub networks with separate, physical network interfaces. Publicly accessible AMI system components include, for example, public web servers. Generally, no AMI system information should be publicly accessible;

- The organization must prevent public access into the organization’s internal AMI system networks except as appropriately mediated and monitored;

- The organization shall limit the number of access points to the AMI system to allow for better monitoring of inbound and outbound network traffic;

- The organization shall implement a managed interface (boundary protection devices in an effective security architecture) with any external telecommunication service, implementing security measures appropriate to the required protection of the integrity and confidentiality of the information being transmitted;

- The AMI system shall deny network traffic by default and allows network traffic by exception (i.e., deny all, permit by exception).

- The organization shall prevent the unauthorized release of information outside of the AMI system boundary or any unauthorized communication through the AMI system boundary when there is an operational failure of the boundary protection mechanisms.

- Field service tools should not interface to the meter through the HAN.

DHS-2.8.7.3 Requirement Enhancements:

None.

DHS-2.8.8 Communication Integrity

DHS-2.8.8.1 Requirement:

The AMI system design and implementation must protect the integrity of electronically communicated information.

DHS-2.8.8.2 Supplemental Guidance:

If the organization is relying on a commercial service provider for communication services as a commodity item rather than a fully dedicated service, it may be more difficult to obtain the necessary assurances regarding the implementation of needed security measures for transmission integrity. When it is infeasible or impractical to obtain the necessary assurances of effective security through appropriate contracting vehicles, the organization must either implement appropriate compensating security measures or explicitly accepts the additional risk. Contracts and other legal documents with vendors should allow for security and integrity testing of products and services used in the AMI systems.

DHS-2.8.8.3 Requirement Enhancements:

- The organization shall employ cryptographic mechanisms to ensure recognition of changes to information during transmission unless otherwise protected by alternative physical measures. The level of protection that is required is determined by the sensitivity of the data being transmitted. (e.g., protective distribution systems).

- The use of cryptography within an AMI system will introduce latency to AMI system communication. The latency introduced from the use of cryptographic mechanisms must not degrade the operational performance of the AMI system or impact personnel safety.

- Failure of a cryptographic mechanism must not create a denial of service or fail to an unprotected open state. Alternative systems should be in place in case of such failure. AMI systems generally support the objectives of availability, integrity, and confidentiality.

DHS-2.8.9 Communication Confidentiality

DHS-2.8.9.1 Requirement:

The AMI system design and implementation must protect the confidentiality of communicated information where necessary.

DHS-2.8.9.2 Supplemental Guidance:

The use of a third-party communication service provider instead of organization owned infrastructure may warrant the use of encryption. The use of cryptographic mechanisms within an AMI system could introduce communications latency due to the additional time and computing resources required to encrypt, decrypt, and authenticate each message. Any latency induced from the use of cryptographic mechanisms must not degrade the operational performance of the AMI system.

DHS-2.8.9.3 Requirement Enhancements:

None.

DHS-2.8.10 Trusted Path

DHS-2.8.10.1 Requirement:

The AMI system must establish trusted communications paths between the user (or agent) and the components making up the AMI system.

DHS-2.8.10.2 Supplemental Guidance:

A trusted path is employed for high-confidence connections between the security functions of the AMI system and the meter. It is recommended that login to the field service tool interface be protected by a trusted path or a compensating control. A trusted path is a mechanism by which a meter can communicate directly with the Trusted Computing Base (TCB) that provides the security functions of the system. This mechanism can only be activated by the authorized user or the TCB. The TCB is the totality of protection mechanisms within an AMI system – including hardware, firmware, and software – the combination of which is responsible for enforcing a security policy. A TCB consists of one or more components that together enforce a unified security policy over a product or system. The ability of a trusted computing base to correctly enforce a security policy depends solely on the mechanisms within the TCB and on the correct input by system administrative personnel and parameters (e.g., a user's clearance) related to the security policy.

DHS-2.8.10.3 Requirement Enhancements:

None.

DHS-2.8.11 Cryptographic Key Establishment and Management

DHS-2.8.11.1 Requirement:

When cryptography is required and employed within the AMI system, the organization shall establish and manage cryptographic keys using automated mechanisms with supporting procedures or manual procedures.

DHS-2.8.11.2 Supplemental Guidance:

Organizations need to select cryptographic protection that matches the value of the information being protected and the AMI system operating constraints. A formal written policy needs to be developed to document the practices and procedures relating to cryptographic key establishment and management. These policies and procedures need to address, under key establishment, such items as the key generation process is in accordance with a specified algorithm and key sizes are based on an assigned standard. Key generation needs to be performed using an effective random number generator. The policies for key management need to address such items as periodic key changes, key destruction, and key distribution in accordance with defined standards.

DHS-2.8.11.3 Requirement Enhancements:

None.

DHS-2.8.12 Use of Validated Cryptography

DHS-2.8.12.1 Requirement:

The organization shall develop and implement a policy governing the use of cryptographic mechanisms for the protection of AMI system information. The organization ensures all cryptographic mechanisms comply with applicable laws, regulatory requirements, directives, policies, standards, and guidance.

DHS-2.8.12.2 Supplemental Guidance:

Any cryptographic modules deployed within an AMI system, at a minimum, must be able to meet the Federal Information Processing Standard (FIPS) 140-2. Assessment of the modules must include validation of the cryptographic modules operating in approved modes of operation. The most effective safeguard is to use a cryptographic module validated by the Cryptographic Module Validation Program. Additional information on the use of validated cryptography can be found at http://csrc.nist.gov/cryptval.

DHS-2.8.12.3 Requirement Enhancements:

- The organization protects cryptographic hardware from physical tampering and uncontrolled electronic connections.

- The organization selects cryptographic hardware with remote key management capabilities.

DHS-2.8.13 Collaborative Computing N/A

DHS-2.8.13.1 Requirement:

The use of collaborative computing mechanisms on AMI components is strongly discouraged and provides an explicit indication of use to the local users.

Alternative statement: Given the current state of this technology and/or the ability to secure it would substantially increase the security risk at this time.

DHS-2.8.13.2 Supplemental Guidance:

Collaborative computing mechanisms include, for example, video and audio conferencing capabilities or instant messaging technologies. Explicit indication of use includes, for example, signals to local users when cameras and/or microphones are activated.

DHS-2.8.13.3 Requirement Enhancements:

If collaborative computing mechanisms are utilized on the AMI system, they are disconnected and powered down when not in use.

DHS-2.8.14 Transmission of Security Parameters

DHS-2.8.14.1 Requirement:

The AMI components must reliably associate security parameters (e.g., security labels and markings) with information exchanged between the enterprise information systems and the AMI system.

DHS-2.8.14.2 Supplemental Guidance:

Security parameters may be explicitly or implicitly associated with the information contained within the AMI system.

DHS-2.8.14.3 Requirement Enhancements:

None.

DHS-2.8.15 Public Key Infrastructure Certificates

DHS-2.8.15.1 Requirement:

The organization shall issue public key certificates under an appropriate certificate policy or obtain public key certificates under an appropriate certificate policy from an approved service provider.

DHS-2.8.15.2 Supplemental Guidance:

Registration to receive a public key certificate needs to include authorization by a supervisor or a responsible official and needs to be accomplished using a secure process that verifies the identity of the certificate holder and ensures that the certificate is issued to the intended party.

DHS-2.8.15.3 Requirement Enhancements:

Any latency induced from the use of public key certificates must not degrade the operational performance of the AMI system.

DHS-2.8.16 Mobile Code

DHS-2.8.16.1 Requirement:

The organization shall:

- Establish usage restrictions and implementation guidance for mobile code technologies based on the potential to cause damage to the AMI system if used maliciously;

- Document, monitor, and manage the use of mobile code within the AMI system.

Appropriate organizational officials should authorize the use of mobile code.

Given the current state of this technology and the limited ability to secure it, use of mobile code substantially increases the security risk at this time.

DHS-2.8.16.2 Supplemental Guidance:

Mobile code technologies include, for example, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations, and VBScript. Usage restrictions and implementation guidance need to apply to both the selection and use of mobile code installed on organizational servers and mobile code downloaded and executed on individual workstations. Procedures need to prevent the development, acquisition, or introduction of unacceptable mobile code within the AMI system. Additional information on risk-based approaches for the implementation of mobile code technologies can be found at https://iase.disa.mil/mcp/index.html.

Mobile code should not be used in the configuration for management interfaces for components on the AMI system. Example: HTTP Web interface for AMI network aggregator.

DHS-2.8.16.3 Requirement Enhancements:

None.

DHS-2.8.17 Voice-Over Internet Protocol

DHS-2.8.17.1 Requirement:

The organization: (i) establishes usage restrictions and implementation guidance for Voice over Internet Protocol (VOIP) technologies based on the potential to cause damage to the information system if used maliciously; and (ii) authorizes, monitors, and limits the use of VOIP within the AMI system.  Given the current state of this technology and/or the ability to secure it would substantially increase the security risk at this time.

DHS-2.8.17.2 Supplemental Guidance:

Generally, VOIP technologies should not be employed on AMI systems. If VOIP is used in support of field services it should not be considered secure. Customer information, passwords or other security information should not be transmitted.

DHS-2.8.17.3 Requirement Enhancements:

None.

DHS-2.8.18 System Connections

DHS-2.8.18.1 Requirement:

All external AMI components and communication connections must be identified and adequately protected from tampering or damage.

DHS-2.8.18.2 Supplemental Guidance:

External access point connections to the AMI system must be secured to protect the system. Access points include any externally connected communication end point (for example, dial-up modems) terminating at any component within the electronic security perimeter. The first step in securing these connections is to identify the connections along with the purpose and necessity of the connection. This information must be documented, tracked, and audited periodically. After identifying these connection points, the extent of their protection needs to be determined. Policies and procedures must be developed and implemented to protect the connection to the business or enterprise information system. This might include disabling the connection except when specific access is requested for a specific need, automatic timeout for the connection, etc.

DHS-2.8.18.3 Requirement Enhancements:

None.

DHS-2.8.19 Security Roles

DHS-2.8.19.1 Requirement:

The AMI system design and implementation must specify the security roles and responsibilities for the users of the system.

DHS-2.8.19.2 Supplemental Guidance:

Security roles and responsibilities for AMI system users must be specified, defined, and implemented based on the sensitivity of the information handled by the AMI system. These roles may be defined for specific task and data handled.

DHS-2.8.19.3 Requirement Enhancements:

None.

DHS-2.8.20 Message Authenticity

DHS-2.8.20.1 Requirement:

The AMI system must provide mechanisms to protect the authenticity of device-to-device communications.

DHS-2.8.20.2 Supplemental Guidance:

Message authentication provides protection from malformed traffic from mis-configured components and malicious entities.

DHS-2.8.20.3 Requirement Enhancements:

Message authentication mechanisms should be implemented at the protocol level for both serial and routable protocols.

DHS-2.8.21 Architecture and Provisioning for Name/Address Resolution Service

DHS-2.8.21.1 Requirement:

AMI components that collectively provide name/address resolution services for an organization must be fault tolerant and implement address space separation.

DHS-2.8.21.2 Supplemental Guidance:

In general, do not use domain name system (DNS) services on an AMI system. Host-based name resolution solutions are the recommended practice. However, if DNS services are implemented, it is recommended to deploy at least two authoritative DNS servers. The DNS configuration on the host will reference one DNS server as the primary source and the other as the secondary source.  Additionally, locate the two DNS servers on different network subnets and separate geographically. If AMI system resources are accessible from external networks, establish authoritative DNS servers with separate address space views (internal and external) to the AMI system resources. The DNS server with the internal view provides name/address resolution services within the AMI system boundary. The DNS server with the external view only provides name/address resolution information pertaining to AMI system resources accessible from external resources. The list of clients who can access the authoritative DNS server with a particular view must also be specified.

DHS-2.8.21.3 Requirement Enhancements:

The use of secure name/address resolution services must not adversely impact the operational performance of the AMI system.

DHS-2.8.22 Secure Name / Address Resolution Service (Authoritative Source)

DHS-2.8.22.1 Requirement:

The AMI system resource (i.e., authoritative DNS server) that provides name/address resolution service must provide additional artifacts (e.g., digital signatures and cryptographic keys) along with the authoritative DNS resource records it returns in response to resolution queries.

DHS-2.8.22.2 Supplemental Guidance:

In general, do not use DNS services on an AMI system. Host-based name resolution solutions are best practice. This requirement enables remote clients to obtain origin authentication and integrity verification assurances for the name/address resolution information obtained through the service. A DNS server is an example of AMI system resource that provides name/address resolution service; digital signatures and cryptographic keys are examples of additional artifacts; and DNS resource records are examples of authoritative data. NIST Special Publication 800-81 provides guidance on secure domain name system deployment.

DHS-2.8.22.3 Requirement Enhancements:

None.

DHS-2.8.23 Secure Name/Address Resolution Service (Recursive or Caching Resolver)

DHS-2.8.23.1 Requirement:

The AMI system resource (i.e., resolving or caching name server) that provides name/address resolution service for local clients shall perform data origin authentication and data integrity verification on the resolution responses it receives from authoritative DNS servers when requested by client systems.

DHS-2.8.23.2 Supplemental Guidance:

In general, do not use DNS services on an AMI system. Host-based name resolution solutions are best practice. A resolving or caching DNS server is an example of an AMI system resource that provides name/address resolution service for local clients and authoritative DNS servers are examples of authoritative sources. NIST Special Publication 800-81 provides guidance on secure domain name system deployment.

DHS-2.8.23.3 Requirement Enhancements:

The AMI system resource that implements DNS services performs data origin authentication and data integrity verification on all resolution responses whether or not local DNS clients (i.e., stub resolvers) explicitly request this function.

ASAP-2.8.24 Secure Name/Address Resolution Service (Address Resolution Tampering)

ASAP-2.8.24.1 Requirement:

The organization shall monitor address resolution traffic to identify potentially malicious patterns of behavior.

ASAP-2.8.24.2 Supplemental Guidance:

Appropriate components or programming must be included within the AMI networks to identify potentially malicious address-resolution behavior (e.g. ARP spoofing/cache poisoning).  Such behavior should be identified, tracked, and the appropriate incident handling team-members alerted.

ASAP-2.8.24.3 Requirement Enhancements:

ARP spoofing and similar attacks may allow an attacker to subvert natural automated network behavior in order to allow the attacker to get "in the middle" of valid communication.  Such attacks, when successful, may allow traffic to be captured, analyzed, and possibly even modified in-transit.

DHS-2.9 Information and Document Management

Information and document management is generally a part of the company records retention and document management system. Digital and hardcopy information associated with the development and execution of AMI components is important, sensitive, and needs to be managed. AMI components design, operations data and procedures, risk analyses, business impact studies, risk tolerance profiles, etc. contain sensitive company information and needs to be protected. Security measures, philosophy, and implementation strategies are other examples. Additionally, business conditions change and require updated analyses and studies. Care is given to protect this information and verify that the appropriate versions are retained. Inherent in this is an information classification system that allows information assets to receive the appropriate level of protection.

The following are the controls for Information and Document Management that need to be supported and implemented by the organization to protect the AMI components.

DHS-2.9.1 Information and Document Management Policy and Procedures

DHS-2.9.1.1 Requirement:

The organization shall develop, disseminate, and periodically review/update:

- A formal, documented, AMI system information and document management policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance.

- Formal, documented procedures to facilitate the implementation of the AMI system information and document management policy and associated system maintenance controls.

DHS-2.9.1.2 Supplemental Guidance:

The organization must ensure that the AMI system information and document management policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The AMI system information and document management policy can be included as part of the general information security policy for the organization. System information and document management procedures can be developed for the security program in general, and for a particular AMI component, when required.

DHS-2.9.1.3 Requirement Enhancements:

None.

DHS-2.9.2 Information and Document Retention

DHS-2.9.2.1 Requirement:

The organization shall manage AMI components related data, including establishing retention policies and procedures for both electronic and paper data, and must manage access to the data based on formally assigned roles and responsibilities.

DHS-2.9.2.2 Supplemental Guidance:

The organization shall develop policies and procedures detailing the retention of company information. These procedures address retention/destruction issues for all applicable information media. Any legal or regulatory requirements are considered when developing these policies and procedures. Information associated with the development and execution of an AMI system is important, sensitive, and needs to be appropriately managed.

DHS-2.9.2.3 Requirement Enhancements:

The organization shall perform legal reviews of the retention policies to ensure compliance with all applicable laws and regulations.

DHS-2.9.3 Information Handling

DHS-2.9.3.1 Requirement:

Organization implemented policies and procedures detailing the handling of information should be developed and periodically reviewed and updated.

DHS-2.9.3.2 Supplemental Guidance:

Written policies and procedures detail access, sharing, copying, transmittal, distribution, and disposal or destruction of AMI system information. These policies or procedures include the periodic review of all information to ensure it is being properly handled. The organization shall protect information against unauthorized access, misuse, or corruption during transportation or transmission. The organization shall distribute or shares information on a need-to-know basis and considers legal and regulatory requirements when developing these policies and procedures.

DHS-2.9.3.3 Requirement Enhancements:

None.

DHS-2.9.4 Information Classification

DHS-2.9.4.1 Requirement:

All information related to AMI components is classified to indicate the protection required commensurate with its sensitivity and consequence.

DHS-2.9.4.2 Supplemental Guidance:

It is recommended that a minimum of three levels of classification be defined for information related to AMI components to indicate the protection required commensurate with its sensitivity and consequence. These levels may be company proprietary, restricted, or public, indicating the need, priority, and level of protection required for that information. These information classification levels provide guidance for access and control to include sharing, copying, transmittal, and distribution appropriate for the level of protection required.

DHS-2.9.4.3 Requirement Enhancements:

None.

DHS-2.9.5 Information Exchange

DHS-2.9.5.1 Requirement:

Formal contractual and confidentiality agreements are established for the exchange of information and software between the organization and external parties.

DHS-2.9.5.2 Supplemental Guidance:

When it is necessary for the AMI components to communicate information to another organization or external party system, the operators need to mutually develop a formal contractual and confidentiality agreement and use a secure method of communication. These formal exchange policies, procedures, and security controls need to be in place to protect the exchange of information through the use of all types of communication facilities.

DHS-2.9.5.3 Requirement Enhancements:

If a specific component needs to communicate with another component outside the AMI system network, communications must be limited to only the components that need to communicate. All other ports and routes must to be locked down or disabled.

DHS-2.9.6 Information and Document Classification

DHS-2.9.6.1 Requirement:

The organization shall develop policies and procedures to classify data, including establishing:

- Retention policies and procedures for both electronic and paper media;

- Classification policies and methods, (e.g., restricted, classified, general, etc.);

- Access and control policies, to include sharing, copying, transmittal, and distribution appropriate for the level of protection required;

- Access to the data based on formally assigned roles and responsibilities for various components of AMI system

DHS-2.9.6.2 Supplemental Guidance:

Companies use both comprehensive information and document management policies for their cyber security management system. Inherent in this is an information classification system that allows information assets to receive the appropriate level of protection. The organization defines information classification levels (e.g., restricted, classified, general, etc.) for access and control to include sharing, copying, transmittal, and distribution appropriate for the level of protection required. The organization also classifies all information (i.e., AMI system design information, network diagrams, process programs, vulnerability assessments, etc.) to indicate the need, priority, and level of protection required commensurate with its sensitivity and consequence.

DHS-2.9.6.3 Requirement Enhancements:

The organization periodically reviews information that requires special control or handling to determine whether such special handling is still required.

DHS-2.9.7 Information and Document Retrieval

DHS-2.9.7.1 Requirement:

The organization shall develop policies and procedures that provide details of the retrieval of written and electronic records, equipment, and other media for components of the AMI system in the overall information and document management policy.

DHS-2.9.7.2 Supplemental Guidance:

The organization shall employ appropriate measures to ensure long-term records information can be retrieved (i.e., converting the data to a newer format, retaining older equipment that can read the data, etc.). Any legal or regulatory requirements are considered when developing these policies and procedures. The organization must take special care to confirm the security, availability, and usability of the AMI components configuration, which includes the logic used in developing the configuration or programming for the life of AMI system.

DHS-2.9.7.3 Requirement Enhancements:

None.

DHS-2.9.8 Information and Document Destruction

DHS-2.9.8.1 Requirement:

The organization shall develop policies and procedures detailing the destruction of written and electronic records, equipment, and other media for the AMI components, without compromising the confidentiality of the data.

DHS-2.9.8.2 Supplemental Guidance:

The organization shall develop policies and procedures detailing the destruction and disposal of written and electronic records, equipment, and other media in the overall information and document management policy. This also includes the method of disposal, such as shredding of paper records, erasing of disks or other electronic media, or physical destruction. All legal or regulatory requirements need to be considered when developing these policies and procedures.

DHS-2.9.8.3 Requirement Enhancements:

None.

DHS-2.9.9 Information and Document Management Review

DHS-2.9.9.1 Requirement:

The organization shall perform periodic reviews of compliance with the AMI system information and document security management policy to ensure compliance with any laws and regulatory requirements.

DHS-2.9.9.2 Supplemental Guidance:

The organization shall regularly review compliance in the information and document management security policy. The compliance review procedure needs to consider all legal and regulatory documentation requirements applicable to the AMI system.

DHS-2.9.9.3 Requirement Enhancements:

None.

DHS-2.9.10 Automated Marking

DHS-2.9.10.1 Requirement:

The components of AMI system shall automatically mark any external data output (physical/paper output) using standard naming conventions to identify any special dissemination, handling, or distribution instructions.

DHS-2.9.10.2 Supplemental Guidance:

Automated marking refers to markings employed on external media (e.g., hardcopy documents output from the AMI components).

DHS-2.9.10.3 Requirement Enhancements:

None.

DHS-2.10 System Development and Maintenance

DHS-2.10.1 System Maintenance Policy and Procedures

DHS-2.10.1.1 Requirement:

The organization shall develop, disseminate, and regularly review and update:

- A documented policy for maintenance of all components of the AMI system. These documents address purpose, scope, roles, responsibilities, coordination among organizational entities, and compliance testing.

- Documented procedures for implementing the maintenance policy.

DHS-2.10.1.2 Supplemental Guidance:

The organization must ensure that the maintenance policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The maintenance policy can be included as part of the general information security policy for the organization. Maintenance policies and procedures can be developed for the security program in general and for particular components of the AMI system when required.

DHS-2.10.1.3 Requirement Enhancements:

None.

DHS-2.10.2 Legacy System Upgrades

DHS-2.10.2.1 Requirement:

The organization shall develop policies and procedures to upgrade all legacy components of the AMI system to include security mitigating measures needed to bring all elements of the AMI system into compliance with current security requirements commensurate with the organization’s risk tolerance for those components.

DHS-2.10.2.2 Supplemental Guidance:

Legacy systems are those components currently in place as part of a working AMI system. In some cases, these systems were installed before there was a concern about system security, and hence, security mitigation measures were not included. The organization determines the current security configuration of legacy components and updates or replaces hardware and software as required.

DHS-2.10.2.3 Requirement Enhancements:

None.

DHS-2.10.3 System Monitoring and Evaluation

DHS-2.10.3.1 Requirement:

The organization shall regularly evaluate all components of the AMI system for security vulnerabilities and for compliance with its maintenance and security policies. All components of the AMI system are updated or replaced to address identified vulnerabilities or non-compliance issues in accordance with the maintenance policy and procedures.

DHS-2.10.3.2 Supplemental Guidance:

The frequency of evaluations is based on the organization's risk mitigation policy. Changing security requirements and discovery of vulnerabilities necessitate a review. These reviews must be carefully planned and documented in accordance with the organization’s maintenance policies and procedures.

DHS-2.10.3.3 Requirement Enhancements:

None.

DHS-2.10.4 Backup and Recovery

DHS-2.10.4.1 Requirement:

The organization shall secure backups of critical software, applications, and data for all components of the AMI system. The organization shall backup all data and applications needed to replace failed components within a reasonable period of time, and as required to satisfy regulatory requirements. Backups shall be physically separated from the operational components.

DHS-2.10.4.2 Supplemental Guidance:

AMI components may be compromised due to an incident or disaster. A copy of essential software and data must to be made, updated regularly, and stored in a secure environment for later use to restore the system to normal operations.

DHS-2.10.4.3 Requirement Enhancements:

None.

DHS-2.10.5 Unplanned System Maintenance

DHS-2.10.5.1 Requirement:

The organization shall review and follow security requirements before undertaking any unplanned maintenance on any component of the AMI system. Unplanned maintenance must be documented and include the following:

- The date and time of maintenance;

- The name of the individual(s) performing the maintenance;

- A description of the maintenance performed; If physical access or modification is required, also document the following:

  - The name of the escort, if necessary;

  - A list of equipment removed or replaced (including identification numbers, if applicable).

DHS-2.10.5.2 Supplemental Guidance:

Unplanned maintenance is required to support system operation in the event of system/component malfunction or failure. Security requirements necessitate that all unplanned maintenance activities use approved contingency plans and document all actions taken to restore operability to the system.

DHS-2.10.5.3 Requirement Enhancements:

The organization documents the decision and justification should unplanned maintenance not be performed after the identification of a security vulnerability.

DHS-2.10.6 Periodic System Maintenance

DHS-2.10.6.1 Requirement:

The organization schedules, performs, and documents routine preventive and regular maintenance for all components of the AMI system in accordance with manufacturer or vendor specifications and/or organizational policies and procedures.

DHS-2.10.6.2 Supplemental Guidance:

Hardware maintenance includes planned replacement of functional equipment (e.g., deployment of new routers). Software maintenance (e.g., patches), like hardware maintenance, requires taking components off-line for some period of time. All maintenance must be approved by the appropriate organization official(s) and planned to avoid significant impact on operations. After maintenance is performed, the organization checks the security features to ensure that they are still functioning properly.

DHS-2.10.6.3 Requirement Enhancements:

The organization keeps a maintenance record for the system that includes the date and time of maintenance, the name of the individual(s) performing the maintenance, the name of the escort (if necessary), a description of the maintenance performed, and a list of equipment removed or replaced (including identification numbers, if applicable).

The organization employs automated mechanisms to schedule and conduct maintenance as required and to create up-to-date, accurate, complete, and available records of all maintenance actions, both needed and completed.

Before disposal of equipment, all critical/sensitive information (e.g., keys) must be removed using approved procedures.

ASAP-2.10.7 Field Tools

ASAP-2.10.7.1 Requirement:

The organization shall approve, manage, protect, and monitor the use of field tools and maintains the integrity of these tools on an ongoing basis.

ASAP-2.10.7.2 Supplemental Guidance:

The intent of this requirement is to address hardware and software connected to component of the AMI system for diagnostics and repairs (e.g., a hardware or software packet sniffer introduced for a particular maintenance activity). Field tools include, for example, diagnostic and test equipment used to conduct maintenance on the network’s software or hardware. Hardware and/or software components that may support maintenance yet are a part of the system (e.g., the software implementing “ping,” “ls,” “ipconfig,” or the hardware and software implementing the monitoring port of an Ethernet switch) are not covered by this requirement.

ASAP-2.10.7.3 Requirement Enhancements:

- The organization shall check all media containing diagnostic and test programs for malicious code before the media are used in the AMI system.

- The organization shall check all field tools that can retain information so that no sensitive information is written on the equipment or the equipment is appropriately sanitized before release; if the equipment cannot be sanitized, the equipment remains within the facility or is destroyed unless an appropriate organization official explicitly authorizes an exception.

DHS-2.10.8 Maintenance Personnel

DHS-2.10.8.1 Requirement:

The organization shall document authorization and approval policies and procedures and maintains a list of personnel authorized to perform maintenance. Only authorized and qualified organization or vendor personnel perform maintenance.

DHS-2.10.8.2 Supplemental Guidance:

Maintenance personnel must have appropriate access authorization when maintenance activities allow access to organizational information that could result in a future compromise of availability, integrity, or confidentiality. When maintenance personnel do not have required access authorizations, organizational personnel with appropriate access authorizations supervise maintenance personnel during the performance of maintenance activities.

DHS-2.10.8.3 Requirement Enhancements:

None.

DHS-2.10.9 Remote Maintenance

DHS-2.10.9.1 Requirement:

The organization shall authorize, manage, and monitor remotely executed maintenance and diagnostic activities on all components of the AMI system. When remote maintenance is completed, the organization or AMI component must terminate all sessions and remote connections invoked in the performance of that activity.

DHS-2.10.9.2 Supplemental Guidance:

Remote maintenance and diagnostic activities are conducted by individuals communicating through an external, non-organization-controlled network (e.g., the Internet). The use of remote maintenance and diagnostic tools must be consistent with organizational policy and documented in the security plan. The organization shall maintain records for all remote maintenance and diagnostic activities.

DHS-2.10.9.3 Requirement Enhancements:

The organization audits all remote maintenance and diagnostic sessions and appropriate organizational personnel review the maintenance records of the remote sessions.

The organization shall address the installation and use of remote maintenance and diagnostic links in the security plan.

DHS-2.12 Incident Response

DHS-2.12.1 Incident Response Policy and Procedures

DHS-2.12.1.1 Requirement: The organization shall develop, disseminate, and periodically review and update:

A documented incident response policy that addresses purpose, scope, roles, responsibilities, coordination among organizational entities, and compliance; and

Documented procedures to facilitate the implementation of the incident response policy and associated incident response controls.

DHS-2.12.1.2 Supplemental Guidance:

The organization must ensure the incident response policy and procedures are consistent with applicable laws, directives, policies, regulations, standards, and guidance.

DHS-2.12.1.3 Requirement Enhancements:

None.

DHS-2.12.2 Continuity of Operations Plan

DHS-2.12.2.1 Requirement:

The organization shall develop and implement a continuity of operations plan dealing with the overall issue of maintaining or re-establishing operation of the AMI system in case of an undesirable interruption. The plan addresses roles, responsibilities, assigned individuals with contact information, and activities associated with restoring system operations after a disruption or failure. Designated officials within the organization review and approve the continuity of operations plan.

DHS-2.12.2.2 Supplemental Guidance:

A continuity of operations plan addresses both business continuity planning and recovery of all vital components of the AMI system.

DHS-2.12.2.3 Requirement Enhancements:

Following a disruption, the organization initiates a root cause analysis for the event and submits any findings from the analysis to the organizations corrective action program.

DHS-2.12.3 Continuity of Operations Roles and Responsibilities

DHS-2.12.3.1 Requirement:

The organization’s continuity of operations plan shall define and communicate the specific roles and responsibilities for each part of the plan in relation to various types of disruptions to the operation of the AMI system.

DHS-2.12.3.2 Supplemental Guidance:

The continuity of operations plan defines the roles and responsibilities of the various employees and contractors in the event of a significant incident. The plans identify responsible personnel to lead the recovery and response effort if an incident occurs.

DHS-2.12.3.3 Requirement Enhancements:

None.

DHS-2.12.4 Incident Response Training

DHS-2.12.4.1 Requirement:

The organization shall train personnel in their continuity of operations plan roles and responsibilities with respect to the AMI system. The organization provides refresher training annually. The training covers employees, contractors, and stakeholders in the implementation of the continuity of operations plan.

DHS-2.12.4.2 Supplemental Guidance:

None.

DHS-2.12.4.3 Requirement Enhancements:

Incident response retraining must include the annual dissemination of information concerning the organizations incident response plan to utility customers.

DHS-2.12.5 Continuity of Operations Plan Testing

DHS-2.12.5.1 Requirement:

The organization shall test the continuity of operations plan to determine its effectiveness and documents the results. Appropriate officials within the organization must review the documented test results and initiate corrective actions if necessary. The organization shall test the continuity of operations plan for the AMI system at least annually, using organization prescribed tests and exercises to determine the plan’s effectiveness and the organization’s readiness to execute the plan.

DHS-2.12.5.2 Supplemental Guidance:

The organization must maintain a list of incident response activities and mitigations for the utility and its customers in accordance with the provisions of the organization incident response policy and procedures. Customers and utility operators need to be notified when testing is scheduled and informed as to how it will be conducted. There are several methods for testing and/or exercising continuity of operations plans to identify potential weaknesses (e.g., full-scale business continuity plan testing, functional/tabletop exercises, etc.). Following the preparation of the various plans, a schedule needs to be developed to review and test each plan and ensure that each still meets the objectives.

DHS-2.12.5.3 Requirement Enhancements:

Utility customers are notified of tests that could affect electrical service.

DHS-2.12.6 Continuity of Operations Plan Update

DHS-2.12.6.1 Requirement:

The organization shall review the continuity of operations plan for the AMI system at least annually and updates the plan to address system, organizational, and technology changes or problems encountered during plan implementation, execution, or testing.

DHS-2.12.6.2 Supplemental Guidance:

Organizational changes include changes in mission, functions, or business processes supported by the AMI system. The organization must communicate the changes to appropriate organizational elements responsible for related plans.

DHS-2.12.6.3 Requirement Enhancements:

Electrical customers will be notified immediately of changes to the plan that may affect them in the event of a contingency or otherwise.

DHS-2.12.7 Incident Handling

DHS-2.12.7.1 Requirement:

All components of the AMI system shall support operations in a safe/limited mode which allows for examination of logs and configuration information, resetting of the component, and enabling and disabling of the component.

DHS-2.12.7.2 Supplemental Guidance:

Incident related information must be available, as appropriate, from all components of the AMI system. This information will include activity logs, network logs, and integrity checks.

DHS-2.12.7.3 Requirement Enhancements:

None.

DHS-2.12.8 Incident Monitoring

DHS-2.12.8.1 Requirement:

The organization must track and document AMI system security incidents on an ongoing basis.

DHS-2.12.8.2 Supplemental Guidance:

None.

DHS-2.12.8.3 Requirement Enhancements:

The communication aggregator shall be able to operate in a safe mode in which communications are relayed from the meter to head end but commands from the head end are not relayed to the individual meters until normal operations are resumed. The component shall also detect and alarm/respond on abnormal command patterns from the head end and abnormal communications patterns from the meters.

DHS-2.12.9 Incident Reporting

DHS-2.12.9.1 Requirement:

The organization promptly reports security incident information to the appropriate authorities.

DHS-2.12.9.2 Supplemental Guidance:

The organization shall develop guidance to determine what is a reportable incident and the granularity of the information reported (e.g., aggregation of common malicious activity) and who to report to (e.g., management, IT security, process safety, control systems engineering, law enforcement agencies, customers). Reporting documents include the details of the incident, the lessons learned, and the course of action to prevent it from occurring again. The types of incident information reported, the content and timeliness of the reports, and the list of designated reporting authorities or organizations are consistent with applicable laws, Executive Orders, directives, policies, regulations, standards, and guidance. In addition to incident information, weaknesses and vulnerabilities in all components of the AMI system need to be reported to appropriate organizational officials in a timely manner to prevent security incidents. Each organization establishes reporting criteria, to include sharing information through appropriate channels. The United States Computer Emergency Readiness Team maintains the Industrial Control System Security Center at http://www.uscert.gov/control_systems.

DHS-2.12.9.3 Requirement Enhancements:

The organization shall employ automated mechanisms to assist in the reporting of security incidents.

DHS-2.12.10 Incident Response Assistance

DHS-2.12.10.1 Requirement:

The AMI component vendor must support customers or customer facing organizations with advice and assistance in the handling and reporting of security incidents as appropriate.

DHS-2.12.10.2 Supplemental Guidance:

Possible implementation of incident response support could include a help desk and/or an assistance group and access to forensic service when required.

DHS-2.12.10.3 Requirement Enhancements:

None.

DHS-2.12.11 Incident Response Investigation and Analysis

DHS-2.12.11.1 Requirement:

The organization shall document its policies and procedures to show that investigation and analysis of incidents are included in the planning process. The procedures ensure that all components of the AMI system are capable of providing event data to the proper personnel for analysis and for developing mitigation steps. The organization must ensure that a dedicated group of personnel is assigned to periodically review the data at a minimum monthly, if not daily or more frequently.

DHS-2.12.11.2 Supplemental Guidance:

The organization shall develop an incident response investigation and analysis program, either internally or externally, to investigate incidents. These investigations consider incidents based on the potential outcome as well as the actual outcome, recognizing that the cyber incident may include intentional and unintentional incidents.

DHS-2.12.11.3 Requirement Enhancements:

- The organization shall develop, test, deploy, and fully document an incident response investigation and analysis process;

- The organization shall specify roles and responsibilities with respect to local law enforcement and/or other critical stakeholders in an internal and shared incident response investigation and analysis program.

DHS-2.12.12 Corrective Action

DHS-2.12.12.1 Requirement:

The organization shall include processes and mechanisms in the planning to ensure that corrective actions identified as the result of a cyber security incident are fully implemented.

DHS-2.12.12.2 Supplemental Guidance:

The organization must review investigation results and determine corrective actions needed to ensure that similar events do not happen again. The organization shall encourage and promote cross-industry incident information exchange and cooperation to learn from the experiences of others.

DHS-2.12.12.3 Requirement Enhancements:

None.

DHS-2.12.13 Alternate Data Storage Sites

DHS-2.12.13.1 Requirement:

The organization shall identify an alternate storage site and initiate necessary agreements to permit the storage of software, data, and configuration information for all components of the AMI system.

DHS-2.12.13.2 Supplemental Guidance:

The frequency of backups of component software and data, and the transfer rate of backup information to the alternate storage site (if so designated) should be consistent with the organization’s recovery time objectives and recovery point objectives.

DHS-2.12.13.3 Requirement Enhancements:

- The organization must identify potential accessibility problems at the alternative storage site in the event of an area-wide disruption or disaster and outlines explicit mitigation actions;

- The organization shall identify an alternate storage site that is geographically separated from the primary storage site so it is not susceptible to the same hazards;

- The organization shall configure the alternate storage site to facilitate timely and effective recovery operations;

- The organization shall identify potential accessibility problems to the alternate storage site in the event of an area-wide disruption or disaster and outlines explicit mitigation actions.

DHS-2.12.14 Alternate Command/Control Methods

DHS-2.12.14.1 Requirement:

The meter shall have a manual connect/disconnect switch and communication ports by which a field tool can be used to extract electric use data in the event that the communication network becomes inoperable or unavailable.

DHS-2.12.14.2 Supplemental Guidance:

The intention is that electrical service can be activated and deactivated and usage records from the meter can be obtained by field personal in the event of the communication network becoming unavailable for prolonged periods of time.

DHS-2.12.14.3 Requirement Enhancements:

For the communication aggregator device, there shall be an alternate command path available. The appropriate alternative command/control method should be chosen based on the criticality of the device. This criterion should be captured in organizational policy and reflect system design requirements.

DHS-2.12.15 Alternate Control Center

DHS-2.12.15.1 Requirement:

The organization shall identify an alternate control center, necessary telecommunications, and initiate necessary agreements to permit the resumption of the operation of the AMI system within an organization-prescribed time period when the primary control center is unavailable.

DHS-2.12.15.2 Supplemental Guidance:

Equipment, telecommunications, and supplies required to resume operations within the organization-prescribed time period need to be available at the alternative control center or by a contract in place to support delivery to the site.

DHS-2.12.15.3 Requirement Enhancements:

- The organization shall identify an alternate control center that is geographically separated from the primary control center so it is not susceptible to the same hazards;

- The organization shall identify potential accessibility problems to the alternate control center in the event of an area-wide disruption or disaster and outline explicit mitigation actions;

- The organization shall develop alternate control center agreements that contain priority-of-service provisions in accordance with the organization’s availability requirements;

- The organization must fully configure the alternate control center and telecommunications so that they are ready to be used as the operational site supporting a minimum required operational capability.

ASAP-2.12.16 Business Data Backup

ASAP-2.12.16.1 Requirement:

The organization shall conduct backups of critical business information stored in all the components of the AMI system: this includes electric use data and other billing information, and any other data essential to the utilities other business functions. These backups must occur on a regular schedule as defined by the organization, and the information is stored at an appropriately secured location.

ASAP-2.12.16.2 Supplemental Guidance:

The frequency of backups and the transfer rate of backup information to alternate storage sites (if so designated) needs to be consistent with the organization’s recovery time objectives and recovery point objectives.

ASAP-2.12.16.3 Requirement Enhancements:

- The organization shall test backup information periodically to verify media reliability and information integrity;

- The organization shall selectively use backup information in the restoration of AMI system functions as part of contingency plan testing;

- The organization shall protect system backup information from unauthorized modification;

- The organization shall employ appropriate mechanisms (e.g., digital signatures, cryptographic hash) to protect the integrity of backups.

DHS-2.12.17 Control System Recovery and Reconstitution

DHS-2.12.17.1 Requirement:

All components of the AMI system shall employ mechanisms to enable recovery and/or reconstitution of the AMI system by authorized personnel after a disruption or failure.

DHS-2.12.17.2 Supplemental Guidance:

The essence of this requirement is that backups made of critical operating software, data, configurations, etc. can be used to restore all components of the AMI system to an operational state.

DHS-2.12.17.3 Requirement Enhancements:

None.

DHS-2.12.18 Fail-Safe Response

DHS-2.12.18.1 Requirement:

All components of the AMI system must fail safe upon the loss of communications with any and all other components of the AMI system.

DHS-2.12.18.2 Supplemental Guidance:

Failures of any and all components of the AMI system shall not jeopardize the Field services devices should have limited capability to make unstable or unsafe settings for the AMI components to which they control.

DHS-2.12.18.3 Requirement Enhancements:

The communication aggregator shall detect and prevent unsafe actions requested by components in the enterprise domain of components in the premise edge and utility edge domains.

DHS-2.14 System and Information Integrity

Maintaining an AMI system, including information integrity, increases assurance that sensitive data have neither been modified nor deleted in an unauthorized or undetected manner. The security controls described under the system and information integrity family provide policy and procedure for identifying, reporting, and correcting AMI system flaws. Controls exist for malicious code detection, spam protection, and intrusion detection tools and techniques. Also provided are controls for receiving security alerts and advisories and the verification of security functions on the AMI system. In addition, there are controls within this family to detect and protect against unauthorized changes to software and data, restrict data input and output, check the accuracy, completeness, and validity of data, and handle error conditions.

DHS-2.14.1 System and Information Integrity Policy and Procedures

DHS-2.14.1.1 Requirement:

The organization must develop, disseminate, and periodically review/updates:

- Formal, documented, system and control integrity policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance;

- Formal, documented procedures to facilitate the implementation, ongoing maintenance, and support of the AMI system and information integrity policy and associated system and information integrity controls.

DHS-2.14.1.2 Supplemental Guidance:

The organization shall ensure the system and information integrity policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The system and information integrity policy can be included as part of the general control security policy for the organization. System and information integrity procedures can be developed for the security program in general, and for a particular AMI component, when required.

DHS-2.14.1.3 Requirement Enhancements:

None.

DHS-2.14.2 Flaw Remediation

DHS-2.14.2.1 Requirement:

The organization shall identify, report, and remediate AMI system flaws (per organizational, legal, and/or regulatory policies).

DHS-2.14.2.2 Supplemental Guidance:

The organization shall identify AMI systems and system components containing software affected by recently announced flaws (and potential vulnerabilities resulting from those flaws). Proprietary software can be found in either commercial/government off-the-shelf component products or in custom-developed applications. The organization (or the software developer/vendor for software developed and maintained by a vendor/contractor) must promptly evaluate newly released security-relevant patches, service packs, and hot fixes and tests them for effectiveness and potential impacts on the organization’s AMI system before installation. Flaws discovered during security assessments, continual monitoring, or under incident response activities also need to be addressed expeditiously. It is generally not recommended to shut down and restart AMI system components when an anomaly is identified.

DHS-2.14.2.3 Requirement Enhancements:

- The organization shall centrally manage the flaw remediation process and installs updates automatically. Organizations must consider the risk of employing automated flaw remediation processes on an AMI system;

- The use of automated flaw remediation processes must not degrade the operational performance of the AMI system;

- The organization must employ automated mechanisms to periodically and upon demand determine the state of AMI system components with regard to flaw remediation.

DHS-2.14.3 Malicious Code Protection

DHS-2.14.3.1 Requirement:

The AMI system must employ malicious code protection.

DHS-2.14.3.2 Supplemental Guidance:

Malicious code protection mechanisms are central to the AMI system design to control the flow of information within the interconnected elements of the system and to detect and eradicate malicious code.

From a system perspective, malicious code protection mechanisms must be deployed in such a manner as to limit the impact of the attack to a small geographical area prior to detection and eradication. These include critical entry and exit points between Wide Area Networks (WAN), Neighborhood Area Networks (NAN), and in-premise networks.

From a host device perspective, one challenge of an AMI system design is that the field deployed host devices are typically not suitable for traditional third party host based malicious code protection mechanisms. This combined with very little or no physical security warrants that emphasis be placed on the risk associated with these widely dispersed assets. For the AMI meters in particular, the Home Area Network (HAN) interface represents and entry point not only into the device but into the utility’s Neighborhood Area Network (NAN) as well. The AMI meter must ensure that no malicious code can pass from the consumer’s HAN to the utility’s NAN. The AMI meter must also protect the consumer’s HAN equipment from any attack which attempts to propagate malicious code utilizing the utility’s NAN.

Field tools represent a potentially higher risk due to their portability and likelihood of being connected to numerous networks. If not properly secured and controlled, they can be a mechanism to bypass security controls and allow malicious code to be transported from one security zone to another.

In all cases, care should be taken if automated response mechanisms are deployed so that receipt of false positives from the malicious code protection mechanisms does not adversely affect the availability of the AMI system.

DHS-2.14.3.3 Requirement Enhancements:

- The use of mechanisms to centrally manage malicious code protection shall not interfere with the reliable operation of the AMI system.

- All signature files and definitions for malicious code detection mechanisms used within the AMI system shall be updated automatically from a centralized managed trusted source.

- Centralized configuration management and change control shall be employed for all AMI system assets.

- Periodic and automatic auditing/verification of configuration (programming parameters, firmware and revision level, etc.) shall be performed for all AMI system assets.

- All detection of and actions taken within the AMI system to respond to malicious code shall be logged to a centralized repository.

- Intrusion Detection System (IDS) capability shall be installed within each Neighborhood Area Network (NAN) network segment to monitor incoming and outgoing network traffic, including anti-virus, anti-spyware and signature and anomaly-based traffic monitors.

- Access Control Lists (ACL) shall be employed at all points which bridge Neighborhood Area Network (NAN) segments to Wide Area Networks (WAN) to limit incoming and outgoing connections to only those necessary to support the AMI system.

- Dynamic packet filtering shall be employed at all points which bridge Neighborhood Area Network (NAN) segments and Wide Area Networks (WAN).

- The transfer of executable files through the perimeters of the Neighborhood Area Network (NAN) and the Wide Area Network (WAN) shall be restricted.

- All components of the AMI system or any device connected to the AMI network shall employ host hardening, including patch application and security-minded configurations of the operating system (OS), browsers, and other network-aware software. All components of the AMI system or any device connected to the AMI network shall employ integrity checking mechanisms for firmware/software.

- All firmware/software shall be scanned prior to loading on any component of the AMI system or device connected to the AMI network.

- The authenticity of all firmware/software shall be verified prior to loading on any component of the AMI system or device connected to the AMI network.

- All AMI components shall be verified to have the proper software revisions and patches prior to being allowed full operation within the AMI network.

- All centrally located components of the AMI system shall employ anti-virus software.

- The AMI meter or gateway device shall not allow uploading of any executable code from the consumer’s HAN.

- Field tools shall have additional control applied as follows:

  - Security updates from the manufacturer of the appropriate operating system, and/or application software, shall be kept current (e.g., patched and updated) on all field tools.

  - Field tools shall employ firewall software or hardware to aid in the prevention of malicious code attacks/infections.

  - Field tools shall employ host hardening, including patch application and security-minded configurations of the operating system (OS), browsers, and other network-aware software.

  - Field tools shall utilize anti-virus, anti-spam, and anti-spyware software.

  - Field tools shall scan removable media devices for malicious code before accessing any data on the media.

  - Field tools shall scan email attachments and shared files of unknown integrity for malicious code before they are opened or accessed.

  - The field tool shall utilize a restricted operating system which only allows execution of known and signed code/applications.

DHS-2.14.4 System Monitoring Tools and Techniques

DHS-2.14.4.1 Requirement:

All components of the AMI system shall log and report all security events and system activities to the AMI management system.

DHS-2.14.4.2 Supplemental Guidance:

Effective monitoring, logging, and alerting of security events requires that all components of the AMI system must be able to generate appropriate logs corresponding to predefined security events.

Including accurate and relevant information in log files is essential. In general, all logs from AMI system components must answer the five basic questions of; Who, What, Where, When, and How. When determining the actions of reading, writing, deleting, and modification of data, it should be possible to determine the process, who owns it, when it was initiated, where the action occurred, and why the process ran. Additionally, all administrative, authentication, authorization, and communication events associated with any AMI system component should be logged and reported.

One challenge when considering an attack on a field-deployed AMI component is that the logging and reporting capability of the component may have be compromised and/or disabled by the attacker. If the monitoring system is only equipped to alert based on logs/reports which are received by the end devices, an attack may go undetected for some period of time if logs representing the security event are not delivered to the central monitoring system.

DHS-2.14.4.3 Requirement Enhancements:

- The monitoring and logging function must not adversely impact the operational performance of the AMI system or component.

- Logs generated by AMI system components shall conform to all applicable recommendations outlined in NIST SP800-92, Guide to Computer Security Log Management.

- The AMI system component shall support standard SYSLOG format (RFC 3164).

- The AMI system component shall provide an authentication mechanism for the logs.

- The AMI system component shall provide a mechanism by which missing logs are detected.

- The AMI system component must be capable of storing a sufficient number of security events in the components buffer to support the system-wide monitoring function.

DHS-2.14.5 Security Alerts and Advisories

DHS-2.14.5.1 Requirement:

The organization:

- Receives AMI system security alerts/advisories regularly and in response to system-based occurrences;

- Issues alerts/advisories to appropriate personnel;

- Takes appropriate actions in response.

DHS-2.14.5.2 Supplemental Guidance:

The organization documents the types of actions to be taken in response to security alerts and advisories. The organization also shall maintain contact with special interest groups (e.g., information security forums) that:

- Facilitate sharing of security-related information (e.g., threats, vulnerabilities, and latest security technologies);

- Provide access to advice from security professionals;

- Improve knowledge of security best practices.

DHS-2.14.5.3 Requirement Enhancements:

The organization shall employ automated mechanisms to make security alert and advisory information available throughout the organization as needed.

DHS-2.14.6 Security Functionality Verification

DHS-2.14.6.1 Requirement:

All components of the AMI system shall employ controls which independently and in concert with the AMI management system verify that that all security functions within the component are in an online/active state. This shall be done upon component and system startup and restart; upon command by a user with appropriate privilege; periodically; and/or at defined time periods.

DHS-2.14.6.2 Supplemental Guidance:

The AMI management system is ultimately tasked with verification of the proper operation of the security functionality however effectively doing so relies heavily on the capabilities embedded within the various components of the AMI system to support this function.

In addition to processing requests initiated by the AMI management system, the AMI system components shall also be able to perform basic automated self-tests independent of the AMI management system. Because of wide geographic deployment and limited physical security of the field deployed AMI components, verification of the proper operation of the security functionality is essential for these components.

DHS-2.14.6.3 Requirement Enhancements:

- All AMI system components shall be capable of periodically performing automated self-test of the security functions at predefined intervals.

  - Any failure of the component self-test shall result in a security event being logged and reported to the appropriate logging system (for further details, see requirement "2.14.4 System Monitoring Tools and Techniques").

  - Any failure of the component self test shall result in the component transitioning to a safe state including:

    - Inhibiting all control capabilities of the component.

    - Inhibiting all communications initiated within the HAN to the NAN.

    - Inhibiting all relaying/repeating functionality of the component.

DHS-2.14.7 Software and Information Integrity

DHS-2.14.7.1 Requirement:

The AMI system must monitor and detect unauthorized changes to software and information.

DHS-2.14.7.2 Supplemental Guidance:

The organization shall employ integrity verification techniques on the AMI system to look for evidence of information tampering, errors, and/or omissions. The organization shall employ good software engineering practices with regard to commercial-off-the-shelf integrity mechanisms (e.g., parity checks, cyclical redundancy checks, cryptographic hashes) and uses tools to automatically monitor the integrity of the IT systems, AMI components, and the applications they host.

DHS-2.14.7.3 Requirement Enhancements:

Although automated tools can be risky for use in AMI system, the following can be considered as appropriate for the AMI system:

- The organization shall reassess the integrity of software and information by performing integrity scans of the AMI system;

- The organization shall employ automated tools that provide notification to appropriate individuals upon discovering discrepancies during integrity verification;

- The organization shall employ centrally managed integrity verification tools;

- The use of integrity verification applications must not adversely impact the operational performance of the AMI system.

DHS-2.14.8 Spam Protection

DHS-2.14.8.1 Requirement:

The AMI system must implement spam protection.

DHS-2.14.8.2 Supplemental Guidance:

The organization shall employ spam protection mechanisms at critical AMI system entry points

(e.g., firewalls, electronic mail servers, remote-access servers) and at workstations, servers, and/or mobile computing devices on the network. The organization uses the spam protection mechanisms to detect and take appropriate action on unsolicited messages transported by electronic mail, electronic mail attachments, Internet access, or other common means. The organization considers using spam protection software products from multiple vendors (e.g., using one vendor for boundary devices and servers and another for workstations).

For an AMI system, the organization should minimize any use of and remove if possible any electronic messaging functions and services (e.g., electronic mail, Internet access). Due to differing operational characteristics between AMI systems and general IT systems, AMI systems do not generally employ spam protection mechanisms. Unusual traffic flow, such as during crisis situations, may be misinterpreted and caught as spam, which can cause issues with the system and possible failure of the system.

DHS-2.14.8.3 Requirement Enhancements:

The organization shall centrally manage spam protection mechanisms. The AMI system must automatically update spam protection mechanisms. Organizations consider the risk of employing mechanisms to centrally manage spam protection on an AMI system. The use of mechanisms to centrally managed spam protection must not degrade the operational performance of the AMI system.

DHS-2.14.9 Information Input Restrictions

DHS-2.14.9.1 Requirement:

The organization shall implement security measures to restrict information input to the AMI system to authorized personnel only.

DHS-2.14.9.2 Supplemental Guidance:

Restrictions on personnel authorized to input information to the AMI system may extend beyond the typical access requirements employed by the system and include limitations based on specific operational or project responsibilities.

DHS-2.14.9.3 Requirement Enhancements:

None.

DHS-2.14.10 Information Input Accuracy, Completeness, Validity, and Authenticity

DHS-2.14.10.1 Requirement:

All AMI system components must employ controls to check information for accuracy, completeness, validity, and authenticity.

DHS-2.14.10.2 Supplemental Guidance:

The design of the AMI system component must consider all valid inputs during its operation. The AMI system component should filter all inputs and allow only those matching a predefined valid set to be processed by the internal hosted application(s). All other inputs not matching this predefined set should be rejected and logged.

DHS-2.14.10.3 Requirement Enhancements:

None.

DHS-2.14.11 Error Handling

DHS-2.14.11.1 Requirement:

All AMI system components shall employ controls to identify and handle error conditions in an expeditious manner without providing information that could be exploited by adversaries.

ASAP/DHS-2.14.11.2 Supplemental Guidance:

The structure and content of error messages displayed by and transmitted from the AMI system components should to be carefully considered by the organization. These error messages must provide timely and useful information without providing potentially harmful information that could be exploited by adversaries. Detailed AMI system component error messages should be revealed only to authorized personnel (e.g., systems administrators, maintenance personnel).

The nature of the AMI system architecture makes it susceptible to observing messages displayed on components and monitoring messages transmitted between components. As such, this opens the risk of an attacker determining specific details about the system or its components by observing error messages on device displays or monitoring error messages transmitted from the field deployed AMI components. Such details can provide hackers important clues on potential flaws in the AMI components.

Risks associated with improper error handling are not limited to those which are transparent to the system operation. AMI system components should not be susceptible to security problems caused by improper error handling, such as:

- Fail-open security check – The component should assume no access until proven otherwise. All security mechanisms should deny access until specifically granted, not grant access until denied, which is a common reason why fail open errors occur.

- Impacts to component resources - Errors that can cause the component to crash or consume significant resources, effectively denying or reducing service to legitimate users.

ASAP-2.14.11.3 Requirement Enhancements:

- Error messages displayed by any field deployed AMI component should not reveal internal details of the component. The component shall provide the user with diagnostic information (e.g., data validation errors), but should NOT provide developer level diagnostic/debug information. Detailed error messages should only be transmitted to the utilities designated logging server.

- The AMI component must not fail in an open condition (grant access unless specifically denied).

DHS-2.14.12 Information Output Handling and Retention

DHS-2.14.12.1 Requirement:

The organization shall handle and retain output from the AMI system in accordance with applicable laws, regulations, standards, and organizational policy, as well as operational requirements of the AMI system.

DHS-2.14.12.2 Supplemental Guidance:

None.

DHS-2.14.12.3 Requirement Enhancements:

None.

DHS-2.15 Access Control

The focus of access control is ensuring that resources are only accessed by the appropriate personnel and that personnel are correctly identified. The first step in access control is creating access control lists with access privileges for personnel. The next step is to implement security mechanisms to enforce the access control lists. Mechanisms also need to be put into place to monitor access activities for inappropriate access attempts. The access control lists need to be managed through adding, altering, and removing access rights as necessary.

Identification and authentication is the process of verifying the identity of a user, process, or component, as a prerequisite for granting access to resources in an AMI system. Identification could use a password, a cryptographic token, or a biometric (e.g. fingerprint). Authentication is the challenge process to prove (validate) the identification provided. An example is using a fingerprint (identification) to access a computer via a biometric device (authentication). The biometric device authenticates the identity of the fingerprint.

DHS-2.15.1 Access Control Policy and Procedures

DHS-2.15.1.1 Requirement:

The organization shall develop, disseminate, and periodically review/update:

- A formal, documented, access control policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance;

- Formal, documented procedures to facilitate the implementation of the access control policy and associated access controls.

Access control policies and procedures for highly-critical management tasks must specify strict security controls commensurate with the criticality of the task - including requirements for physical presence at a management console situated in a physically secure location, multiple levels of approval/authorization (by those with appropriate organizational roles), and strong multi-factor authentication.

DHS-2.15.1.2 Supplemental Guidance:

The organization shall ensure that access control policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The access control policy can be included as part of the general information security policy for the organization. Access control procedures can be developed for the security program in general, and for a particular AMI component, when required.

It is recommended that the access control policy include the requirement that the HAN interface shall pass no control signals to the utility.  Only informational signals may be passed on to the utility which shall base no control decisions on HAN-sourced communications without confirmation that the HAN-sourced information is strongly authenticated and consistent with information provided from utility-owned devices within utility-controlled security domains (physical and logical).  The utility shall have the ability to set the HAN interface to ignore (i.e., filter) non-authenticated HAN communications or communications from specific HAN-devices when it deems such communications to be a threat to security or safety.

DHS-2.15.1.3 Requirement Enhancements:

None.

DHS-2.15.2 Identification and Authentication Policy and Procedures

DHS-2.15.2.1 Requirement:

The organization shall develop, disseminate, and periodically review/update:

- A formal, documented, identification and authentication policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance;

- Formal, documented procedures to facilitate the implementation of the identification and authentication policy and associated identification and authentication controls.

All communications between AMI components must be strongly authenticated. Any communications upon which critical management and control decisions are based must be confirmed by multiple independent means (which may include "out-of-band" communications).

Any communication to be passed onto the utility by the HAN-interface must be strongly authenticated and non-control in nature.

DHS-2.15.2.2 Supplemental Guidance:

The organization shall ensure the identification and authentication policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The identification and authentication policy can be included as part of the general security policy for the organization. Identification and authentication procedures can be developed for the security program in general, and for a particular AMI system, when required.

DHS-2.15.2.3 Requirement Enhancements:

None.

DHS-2.15.3 Account Management

DHS-2.15.3.1 Requirement:

The organization shall manage AMI system accounts, including establishing, activating, modifying, reviewing, disabling, and removing accounts. The organization reviews AMI system accounts, policies, and procedures at least annually, with the frequency depending on criticality.

DHS-2.15.3.2 Supplemental Guidance:

Account management includes the identification of account types (i.e., individual, group, role-based, device-based, and system), establishment of conditions for group membership, and assignment of associated authorizations. The organization shall identify authorized users of the AMI system and specifies access rights and privileges; i.e., access control list. The organization shall grant access to the AMI system based on:

- A valid need-to-know/need-to-share basis that is determined by assigned official duties and that satisfies all personnel security criteria;

- Intended system use. The organization must require proper identification for requests to establish AMI system accounts and must approve all such requests. The organization specifically authorizes and monitors the use of guest/anonymous accounts and removes, disables, or otherwise secures unnecessary accounts. The organization ensures that account managers for the AMI system are notified when users are terminated or transferred and associated accounts are removed, disabled, or otherwise secured. Account managers are also notified when users’ AMI system usage or need-to-know/need-to-share changes. In cases where accounts are role-based, i.e., the workstation, hardware, and/or field devices define a user role, access to the AMI system includes physical security policies and procedures based on organization risk assessment. In cases where physical access to the workstation, hardware, and/or field devices predefines privileges, the organization must implement physical security policies, and procedures based on organization risk assessment. Account management may include additional account types (e.g., role-based, device-based, attribute-based). The organization removes, disables, or otherwise secures default accounts (e.g., maintenance).

- Default passwords are changed.

DHS-2.15.3.3 Requirement Enhancements:

- The organization shall employ automated mechanisms to support the management of AMI system accounts. For some AMI components (e.g., field devices), account management may have to be performed manually, where automated mechanisms are not available.

- The AMI system must automatically terminate temporary and emergency accounts.

- The AMI system must automatically disable inactive accounts.

- The organization must employ automated mechanisms to audit account creation, modification, disabling, and termination actions and to notify, as required, appropriate individuals.

- The organization must ensure default passwords are changed.

DHS-2.15.4 Identifier Management

DHS-2.15.4.1 Requirement:

The organization shall manage user identifiers by:

- Uniquely identifying each user;

- Verifying the identity of each user;

- Receiving authorization to issue a user identifier from an appropriate organization official;

- Ensuring that the user identifier is issued to the intended party;

- Disabling user identifier after a pre-determined time period of inactivity;

- Archiving user identifiers.

DHS-2.15.4.2 Supplemental Guidance:

All actions within an AMI system should be traceable to an individual user.  Guest, Anonymous, and Group accounts should not be used.  "Root" or similar administrative accounts should not be used for normal operation.  For administrative tasks, individual accounts should be used in conjunction with "runas" or "sudo" or similar logging access-control mechanism.

For some AMI components, the capability for immediate operator interaction is critical. Local emergency actions for the AMI system must not be significantly hampered by identification requirements. Access to these systems may be restricted by appropriate physical security mechanisms, and should cause immediate alerting of security personnel.

Failure of identification system should not fail to an open unprotected state.  It should fail to a protected, recoverable backup state.

DHS-2.15.4.3 Requirement Enhancements:

None.

DHS-2.15.5 Authenticator Management

DHS-2.15.5.1 Requirement:

The organization shall manage AMI system authenticators by:

- Defining initial authenticator content criteria;

- Establishing administrative procedures for initial authenticator distribution, for lost/compromised, or damaged authenticators, and for revoking authenticators;

- Changing default authenticators upon AMI system installation;

- Changing/refreshing authenticators periodically.

- All components must be able to support these organizational activities.

- All permissions associated with authenticators should be maintained at as low a level as possible so that, in case of compromise, an attacker's access would be limited (see DHS-2.15.9 Least Privilege)

DHS-2.15.5.2 Supplemental Guidance:

System authenticators include, for example, cryptographic tokens, PKI certificates, biometrics, passwords, and key cards. Users take reasonable measures to safeguard authenticators including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others, and reporting lost or compromised authenticators immediately.

Passwords must not be embedded into tools, source code, scripts, aliases or shortcuts. Many AMI components and software are shipped with factory default authentication credentials to allow for initial installation and configuration. However, factory default authentication credentials are often well known, easily discoverable, present a great security risk and therefore should be changed.

DHS-2.15.5.3 Requirement Enhancements:

For symmetric/password-based authentication, the AMI system:

- Protects passwords from unauthorized disclosure and modification when stored or transmitted;

- Prohibits passwords from being displayed when entered;

- Enforces password minimum and maximum lifetime restrictions;

- Prohibits password reuse for a specified number of generations.

For asymmetric/PKI-based authentication, the AMI system:

- Validates certificates by constructing a certification path to an accepted trust anchor;

- Establishes control of the corresponding private key;

- Maps the authenticated identity to the user account.

- Restricts field tools password and keys life-span in case they are stolen.

DHS-2.15.6 Supervision and Review

DHS-2.15.6.1 Requirement:

The organization must supervise and review the activities of users with respect to the enforcement and usage of AMI system access control. AMI components must provide auditing capability specified in section DHS-2.16.

DHS-2.15.6.2 Supplemental Guidance:

The organization shall review audit records (e.g., user activity logs) for inappropriate activities in accordance with organizational procedures. The organization must investigate any unusual AMI system-related activities and periodically review changes to access authorizations. The organization shall review the activities of users with significant roles and responsibilities for the AMI system more frequently. The extent of the audit record reviews is based on the impact level of the AMI system. For example, for low-impact systems it is not intended that security logs be reviewed frequently for every workstation but rather at central points such as a web proxy or email servers and when specific circumstances warrant review of other audit records.

The organization shall have in place policies and procedures that deal specifically with breaches in security, that detail specifically what actions are to occur to secure the breach and investigate any damage.  This plan should also include who is responsible for patches and updates and how they are to occur.

DHS-2.15.6.3 Requirement Enhancements:

The organization should employ automated mechanisms to facilitate the review of user activities on the AMI system.

DHS-2.15.7 Access Enforcement

DHS-2.15.7.1 Requirement:

AMI components must enforce assigned authorizations for controlling access to the system in accordance with applicable policy.

Access to AMI components that perform managed services (e.g. Field Tool) must be tightly controlled. Interfaces of particular interest are AMI components that use a PC (or laptop) or mobile devices for interfacing with control functions.

DHS-2.15.7.2 Supplemental Guidance:

Access control policies (e.g., identity-based policies, role-based policies, rule-based policies) and associated access enforcement mechanisms (e.g., access control lists, access control matrices, and cryptography) are employed by organizations to control access to the AMI system. The organization shall consider the implementation of a controlled, audited, and manual override of automated mechanisms in the event of emergencies or other serious events.

The functionality of field tools and other systems which perform managed services must be limited to the bare minimum to perform the needed task. E-mail and web functions should be removed or limited to access only an approved list. Other applications not required to perform the functions must be removed.

DHS-2.15.7.3 Requirement Enhancements:

- The AMI system shall restrict access to privileged functions (deployed in hardware, software, and firmware) and security-relevant information to explicitly authorized personnel. Explicitly authorized personnel include, for example, AMI system operators, security administrators, system and network administrators, and other privileged users who have access to system control, monitoring, or administration functions. Access to privileged functions by privileged users may also be restricted based on components (e.g., remote terminal units and field devices).

- The AMI system must requires dual authorization, based on approved organization procedures, to privileged functions that have impacts on facility, human, and environmental safety. The utility should develop and implement a procedure that can be executed in times of emergency for access to otherwise restricted passwords and keys

- Access enforcement mechanisms must not adversely impact the operational performance of the AMI system.

- The meter IR port must be protected from unauthorized access.  Permit only the most restrictive set of rights/privileges or accesses needed by users for the performance of specified tasks (see section DHS-2.15.9 "Least Privilege").

- The meter HAN interface must be protected from unauthorized access. Permit only the most restrictive set of rights/privileges or accesses needed by users for the performance of specified tasks (see section DHS-2.15.9 "Least Privilege").

- AMI field tool must require access control to utilize the tool. Field service tool should not save or store customer information, passwords, encryption key, or any other information that may compromise the AMI system or network.

- The HAN interface shall never allow HAN-devices access to utility control functions.

DHS-2.15.8 Separation of Duties

DHS-2.15.8.1 Requirement:

The organization shall enforce separation of duties through assigned access authorizations.

DHS-2.15.8.2 Supplemental Guidance:

The organization must establish appropriate divisions of responsibility and separate duties as needed to eliminate conflicts of interest in the responsibilities and duties of individuals. Access control software needs to be on the AMI system that prevents users from having all of the necessary authority or information access to perform fraudulent activity without collusion. Examples of separation of duties include 1) mission functions and distinct AMI system support functions are divided among different individuals/roles; 2) different individuals perform AMI system support functions (e.g., system management, systems programming, quality assurance/testing, configuration management, and network security); and 3) security personnel who administer access control functions must not administer audit functions.

DHS-2.15.8.3 Requirement Enhancements:

None.

DHS-2.15.9 Least Privilege

DHS-2.15.9.1 Requirement:

The organization shall enforce the most restrictive set of rights/privileges or accesses to users or workstations (or processes acting on behalf of users) for the performance of specified tasks. The AMI components shall support this organizational requirement.

DHS-2.15.9.2 Supplemental Guidance:

The organization shall employ the concept of least privilege for specific duties and AMI components (including specific ports, protocols, and services) in accordance with risk assessments as necessary to adequately mitigate risk to organizational operations, organizational assets, and individuals.

DHS-2.15.9.3 Requirement Enhancements:

None.

DHS-2.15.10 User Identification and Authentication

DHS-2.15.10.1 Requirement:

The AMI system shall uniquely identify and authenticate users (or processes acting on behalf of users).

DHS-2.15.10.2 Supplemental Guidance:

Users must be uniquely identified and authenticated for all accesses other than those accesses explicitly identified and documented by the organization in accordance with security control.

Authentication of user identities shall be accomplished through the use of passwords, tokens, biometrics, or in the case of multifactor authentication, some combination of these. In addition to identifying and authenticating users at the AMI system level (i.e., at system logon), identification and authentication mechanisms are employed at the application level, when necessary, to provide increased information security for the organization.

Where users function as a single group (e.g., control room operators), user identification and authentication may be role-based, group-based, or device-based. For some components of AMI system, the capability for immediate operator interaction is critical. The utility must develop and implement a procedure that can be executed in times of emergency for access to otherwise restricted passwords and keys. Access to these systems may be restricted by appropriate physical security mechanisms.

DHS-2.15.10.3 Requirement Enhancements:

Remote user access to AMI system components is only enabled when necessary, approved, and authenticated.

DHS-2.15.11 Permitted Actions without Identification or Authentication

DHS-2.15.11.1 Requirement:

The organization shall identify, document, and provide security justification for specific user actions that can be performed on the AMI system without identification or authentication.

DHS-2.15.11.2 Supplemental Guidance:

The use of anonymous accounts, public accounts, and guest accounts is prohibited.

The HAN interface should not permit any actions (including communications) without identification or authentication. AMI components that perform management services (e.g. Field Tool) shall not be permitted to perform any actions without identification or authentication.

DHS-2.15.11.3 Requirement Enhancements:

None.

DHS-2.15.12 Device Identification and Authentication

DHS-2.15.12.1 Requirement:

The AMI system must employ a mechanism to identify and authenticate specific components before establishing a connection. In particular, the HAN interface requires strong authentication, as do components that perform management services (e.g. Field Tool).

DHS-2.15.12.2 Supplemental Guidance:

The strength of the device authentication mechanism is based on the security categorization of the AMI system. Automatic equipment identification may be considered as a means to authenticate connections. Field devices must have the capability to support authentication mechanisms

DHS-2.15.12.3 Requirement Enhancements:

None.

DHS-2.15.13 Authenticator Feedback

DHS-2.15.13.1 Requirement:

The authentication mechanisms in the AMI component/system must obfuscate feedback of authentication information during the authentication process to protect the information from possible exploitation/use by unauthorized individuals. This applies to authentication by one component to another as well as by individuals.

DHS-2.15.13.2 Supplemental Guidance:

The AMI component/system shall obscure feedback of authentication information during the authentication process (e.g., displaying asterisks when a user types in a password). The feedback from the AMI component/system does not provide information that would allow an unauthorized user to compromise the authentication mechanism.

AMI components involved in authentication must not at any time pass key or token information in an unencrypted format.

Authentication mechanisms should not provide differences which indicate whether the failure is due to invalid userid or password/key.

DHS-2.15.13.3 Requirement Enhancements:

None.

DHS-2.15.14 Cryptographic Module Authentication

DHS-2.15.14.1 Requirement:

The AMI component/system shall employ authentication methods that meet the requirements of applicable laws, executive orders, directives, policies, regulations, standards, and guidance for authentication to a cryptographic module. (E.g. …must comply with FIPS 140-2 and NERC security authentication method requirements.)

DHS-2.15.14.2 Supplemental Guidance:

None.

DHS-2.15.14.3 Requirement Enhancements:

Failure of cryptographic module authentication must not create a denial of service or adversely impact the operational performance of the AMI system. The system must also not fail to an open unprotected state. Systems critical to overall performance, reliability, safety, and security must provide safe secure failover protection in case of primary authentication failure.

DHS-2.15.15 Information Flow Enforcement

DHS-2.15.15.1 Requirement:

The AMI component/system shall enforce assigned authorizations for controlling the flow of information within the system and between interconnected systems in accordance with applicable policy. As stated earlier, the HAN interface shall not pass control signals from the HAN to the utility.

DHS-2.15.15.2 Supplemental Guidance:

Information flow control regulates where information is allowed to travel within an AMI system and between AMI components (as opposed to who is allowed to access the information) and without explicit regard to subsequent accesses to that information. A few general examples of possible restrictions that are better expressed as flow control than access control are: keeping export controlled information from being transmitted in the clear to the Internet, blocking outside traffic that claims to be from within the organization and not passing any web requests to the Internet that are not from the internal web proxy. Information flow control policies and enforcement mechanisms are commonly employed by organizations to control the flow of information between designated sources and destinations (e.g., networks, individuals, devices) within AMI system and between interconnected systems. Flow control is based on the characteristics of the information and/or the information path. Specific examples of flow control enforcement can be found in boundary protection devices (e.g., proxies, gateways, guards, encrypted tunnels, firewalls, and routers) that employ rule sets or establish configuration settings that restrict AMI system services or provide a packet-filtering capability.

DHS-2.15.15.3 Requirement Enhancements:

- The information system shall implement information flow control enforcement using explicit labels on information, source, and destination objects as a basis for flow control decisions. Information flow control enforcement using explicit labels is used, for example, to control the release of certain types of information.

- The information system shall implement information flow control enforcement using protected processing domains (e.g., domain type-enforcement) as a basis for flow control decisions.

- The information system shall implement information flow control enforcement using dynamic security policy mechanisms as a basis for flow control decisions.

DHS-2.15.16 Passwords

DHS-2.15.16.1 Requirement:

The AMI components that support passwords should enforce a level of complexity based on the criticality level of the device/system. Default passwords of applications, operating systems, etc must be changed immediately. Passwords need to be changed regularly and systems should enforce an expiration policy based on the criticality level of the AMI component/system. Passwords must not to be embedded into tools, source code, scripts, aliases or shortcuts.

DHS-2.15.16.2 Supplemental Guidance:

- Default passwords of applications, operating systems, database management systems, or other programs must be changed immediately after installation.

- The organization must replace default usernames whenever possible. Passwords need to be allocated, protected, and used based on the criticality level of the systems to be accessed.

- The organization shall develop policies that stipulate the complexity (min/max length, combination of lower/upper case, numerals, special characters, etc.) level of the password for each criticality level. Short or easily guessed passwords are prohibited. Passwords can be a means of system protection when properly generated and used. Although passwords are not advisable in all AMI system applications, there are some cases where they are of benefit such as for remote access. These passwords are developed to meet defined metrics.

- Good security practices must be followed in the generation of passwords. Passwords should not easily be associated with the user or the organization and follow appropriate complexity rules. Initial or default passwords must be changed immediately on first log-in. Following generation, passwords shall not be sent across any network unless protected by encryption or salted cryptographic hash specifically designed to prevent replay attacks.

- Passwords must be transferred to the user via secure media and the recipient must be verified. The logon ID and password must be never combined in the same communication.

- The authority to keep and change high-level passwords shall be given to a trusted employee who is available during emergencies.

- A log for master passwords needs to be maintained separately from the AMI system, possibly in a notebook in a vault or safe.

- Passwords must be changed regularly and expire when the user leaves the organization or after an extended period of inactivity.

- Users are responsible for their passwords and are instructed not to share them or write them down, and need to be aware of their surroundings when entering passwords. If the operating system supports encryption, stored passwords are encrypted. Passwords must not to be embedded into tools, source code, scripts, aliases or shortcuts.

DHS-2.15.16.3 Requirement Enhancements:

None.

DHS-2.15.17 System Use Notification

DHS-2.15.17.1 Requirement:

When appropriate, the AMI component or system shall display an approved, system use notification message before granting access.

DHS-2.15.17.2 Supplemental Guidance:

The organization or the AMI system displays an approved, system-use notification message at the time of AMI system logon informing the user:

- Of the organization’s privacy policy before granting system access to potential users and/or workstations;

- That system usage may be monitored, recorded, and subject to audit;

- That unauthorized use of the system is prohibited and subject to criminal and civil penalties;

- That use of the system indicates consent to monitoring and recording.

The system use notification message provides appropriate privacy and security notices (based on organization’s associated privacy and security policies or summaries) and remains on the screen until the user takes explicit actions to log on to AMI system. Privacy and security policies are consistent with applicable federal and state laws, organization directives, policies, regulations, standards, and guidance.

DHS-2.15.17.3 Requirement Enhancements:

None.

DHS-2.15.18 Concurrent Session Control

DHS-2.15.18.1 Requirement:

The AMI components limit the number of concurrent sessions for any user on the AMI system based on the criticality level of the component.

The organization limits the number of concurrent sessions for any user on the AMI system.

DHS-2.15.18.2 Supplemental Guidance:

None.

DHS-2.15.18.3 Requirement Enhancements:

None.

DHS-2.15.19 Previous Logon Notification

DHS-2.15.19.1 Requirement:

The AMI components shall notify the user, upon successful logon, of the date and time of the last logon and the number of unsuccessful logon attempts since the last successful logon based on the criticality level of the component.

The AMI system notifies the user, upon successful logon, of the date and time of the last logon and the number of unsuccessful logon attempts since the last successful logon.

DHS-2.15.19.2 Supplemental Guidance:

None.

DHS-2.12.18.3 Requirement Enhancements:

None.

DHS-2.15.20 Unsuccessful Login Attempts

DHS-2.15.20.1 Requirement:

The AMI components shall limit the number of consecutive invalid access attempts by a user during a given time period based on the criticality level of the component. The component disables user accounts when the maximum number of unsuccessful attempts is exceeded and logs all unsuccessful login attempts.

The AMI system shall limit the number of consecutive invalid access attempts by a user during a given time period. The AMI system must temporarily disable the user account when the maximum number of unsuccessful attempts is exceeded and logs all unsuccessful login attempts.

DHS-2.15.20.2 Supplemental Guidance:

Because of the potential for denial of service, automatic lockouts initiated by the AMI system are usually temporary and automatically released after a predetermined time period established by the organization. Permanent automatic lockouts initiated by the AMI system must be carefully considered before being used due to safety considerations and the potential for denial of service.

DHS-2.12.20.3 Requirement Enhancements:

The AMI system must automatically lock the account/node until released by an administrator when the maximum number of unsuccessful attempts is exceeded.

DHS-2.15.21 Session Lock

DHS-2.15.21.1 Requirement:

After a predetermined period of inactivity, the AMI system shall prevent further access to the system by initiating a session lock that remains in effect until the user reestablishes access using appropriate identification and authentication procedures.

DHS-2.15.21.2 Supplemental Guidance:

Users can directly initiate session lock mechanisms. A session lock is not a substitute for logging out of the AMI system.

DHS-2.15.21.3 Requirement Enhancements:

None.

DHS-2.15.22 Remote Session Termination

DHS-2.15.22.1 Requirement:

The AMI system must automatically terminate a remote session after a defined period of inactivity for workstations that are used for AMI system monitoring and maintenance activities based on the risk assessment of the AMI system and the organization’s security policy.

On critical high-risk systems it may also be advised that the ports and/or software applications for remote access must be disabled and in some cases physically disconnected

DHS-2.15.22.2 Supplemental Guidance:

A remote session is initiated whenever an organizational AMI system is accessed by a user (or an information system) communicating through an external, non-organization-controlled network (e.g., the Internet). Some AMI components may not or cannot allow sessions to be terminated.

DHS-2.15.22.3 Requirement Enhancements:

Automatic session termination applies to local and remote sessions. The AMI system terminates a network connection at the end of a session or after a period of inactivity per organization policy and procedures.

DHS-2.15.23 Remote Access Policy and Procedures

DHS-2.15.23.1 Requirement:

The organization shall develop a formal written policy and appropriate security procedures to address and protect against the risks of remote access to the AMI system, field devices, and communication facilities.

DHS-2.15.23.2 Supplemental Guidance:

In many cases, AMI components are not located within the boundaries of the control room or where there may be a need for access to equipment remote from the user, including telecommuting or mobile computing. A formal, written procedure is required to address access to systems remote from the user. This policy might include system locking of an interactive session after a specified period of user inactivity, using encrypted password setting on boot up and login for computers not in the control room, encrypted file system, callback and authentication on modems, or the inactivation or disconnection from the network when connections are not required. Appropriate organization officials need to authorize each remote access method for the AMI system and authorize only the necessary users, based on their roles and responsibilities, for access methods identified in the risk assessment.

DHS-2.15.23.3 Requirement Enhancements:

None.

DHS-2.15.24 Remote Access

DHS-2.15.24.1 Requirement:

Remote access to the AMI components must be enabled only when appropriate and with a level of authentication appropriate to the criticality of the system.

The organization shall authorize, monitor, and manage all methods of remote access to the AMI system.

DHS-2.15.24.2 Supplemental Guidance:

The organization shall document, monitor, and manage all methods of remote access (e.g., dialup, Internet, physical) to the AMI system. Appropriate authentication methods are required to adequately secure remote access.

Remote access is any access to the AMI system or components by a user (or an information system) communicating through an external, non-organization-controlled network (e.g., the Internet). Remote access includes wireless and access via portable and mobile devices. Examples of remote access methods include dial-up, broadband, and wireless. Remote access security requirements are applicable to AMI components other than public web servers or systems specifically designed for public access. The organization restricts access achieved through dial-up connections (e.g., limiting dial-up access based upon source of request) or protects against unauthorized connections or subversion of authorized connections (e.g., using virtual private network technology).

Remote access to AMI component locations (e.g., control center, field locations) is only enabled when necessary, approved, and authenticated. The organization considers multifactor authentication for remote user access to the AMI system.

DHS-2.15.24.3 Requirement Enhancements:

- The organization shall employ automated mechanisms to facilitate the monitoring and control of remote access methods.

- The organization shall use cryptography to protect the confidentiality and integrity of remote access sessions. Any latency induced from the use of encryption, must not degrade the operational performance of the AMI system.

- The organization shall provide remote accesses through a limited number of managed access control points.

- The organization shall permit remote access for privileged functions only for compelling operational needs and documents the rationale for such access in the security plan for the AMI system.

DHS-2.15.25 Access Control for Portable and Mobile Devices

DHS-2.15.25.1 Requirement:

The organization must:

- Establish use restrictions and implementation guidance for all portable media and mobile IT devices

- Document, monitor, log, and limit access of these portable media and mobile devices to AMI system. Appropriate organizational officials authorize the use of portable and mobile devices per organization’s established security policy and procedures.

DHS-2.15.25.2 Supplemental Guidance:

Portable media and mobile devices (e.g., notebook computers, workstations, and personal digital assistants) are allowed access to organizational networks and AMI system by meeting organizational security policies and procedures. Security policies and procedures include such activities as scanning the components for malicious code, updating virus protection software, scanning for critical software updates and patches, conducting primary operating system (and possibly other resident software) integrity checks, and disabling unnecessary hardware (e.g., wireless).

Organizations must disable unused or unnecessary I/O ports.

DHS-2.15.25.3 Requirement Enhancements:

None.

DHS-2.15.26 Wireless Access Restrictions

DHS-2.15.26.1 Requirement:

The organization must:

- Establish use restrictions and implementation guidance for wireless technologies

- Authorize, monitor, and manage wireless access to the AMI system.

DHS-2.15.26.2 Supplemental Guidance:

The organization shall use authentication and cryptography or enhanced defense mechanisms to protect wireless access to the AMI system.  Wireless technologies include, but are not limited to, microwave, satellite, packet radio [UHF/VHF], 802.11, 802.15, 802.16, cellular, ZigBee, ISA100, WiHart, and Bluetooth.

DHS-2.15.26.3 Requirement Enhancements:

- The organization shall use authentication and encryption to protect wireless access to the AMI system. Any latency induced from the use of encryption, must not degrade the operational performance of the AMI system.

- The organization shall scan for unauthorized wireless access points at a specified frequency and takes appropriate action if such access points are discovered. Organizations conduct a thorough scan for unauthorized wireless access points in facilities containing high-impact AMI components. The scan is not limited to only those areas within the facility containing the high-impact AMI components.

DHS-2.15.27 Personally Owned Information

DHS-2.15.27.1 Personally Owned Information

DHS-2.15.27.1 Requirement:

The organization must restrict the use of personally owned information copied to the AMI system or AMI system user workstation that is used for official organization business. This includes the processing, storage, or transmission of organization business and critical AMI system information. The terms and conditions need to address, at a minimum;

- The types of applications that can be accessed from personally owned IT, either remotely or from within the AMI system;

- The maximum security category of information that can processed, stored, and transmitted;

- How other users of the personally owned AMI components will be prevented from accessing organization information;

- The use of virtual private networking (VPN) and firewall technologies;

- The use of and protection against the vulnerabilities of wireless technologies;

- The maintenance of adequate physical security mechanisms;

- The use of virus and spyware protection software; and

- How often the security capabilities of installed software are to be updated (e.g., operating system and other software security patches, virus definitions, firewall version updates, malware definitions).

DHS-2.15.27.2 Supplemental Guidance:

The organization must establish strict terms and conditions for the use of personally owned information on AMI components.

DHS-2.15.27.3 Requirement Enhancements:

None.

DHS-2.15.28 External Access Protections

DHS-2.15.28.1 Requirement:

The organization shall employ mechanisms in the design and implementation of an AMI system to restrict public access to the AMI system from the organization’s enterprise network.

DHS-2.15.28.2 Supplemental Guidance:

Public access is defined as access from the enterprise system. Care should be taken to ensure data shared with the enterprise system are protected for integrity of the information and applications. Public access to the AMI system to satisfy business requirements needs to be limited to read only access through the corporate enterprise systems via a demilitarized zone (DMZ). The organization shall explicitly allow necessary network protocols in the DMZ; blocks or filters unnecessary protocols, configure firewalls to block inbound connections, limits outbound connections to only those specifically required for operations, and eliminates network connections that bypass perimeter protection mechanisms (e.g. firewall, VPN, DMZ).

DHS-2.15.28.3 Requirement Enhancements:

None.

DHS-2.15.29 Use of External Information Control Systems

DHS-2.15.29.1 Requirement:

The organization shall establish terms and conditions for authorized individuals to:

- Access the AMI system from an external system;

- Process, store, and/or transmit organization-controlled information using an external system.

DHS-2.15.29.2 Supplemental Guidance:

External systems are systems or components of systems that are outside of the accreditation boundary established by the organization and for which the organization typically has no control over the application of required security levels or the assessment of security effectiveness. External information systems include, but are not limited to, personally owned information systems (e.g., computers, cellular telephones, or personal digital assistants); privately owned computing and communications components resident in commercial or public facilities (e.g., hotels, convention centers, or airports); information systems owned or controlled by nonfederal governmental organizations; and federal information systems that are not owned by, operated by, or under the direct control of the organization.

Authorized individuals include organizational personnel, contractors, or any other individuals with authorized access to the organizational information system. This control does not apply to the use of external information systems to access organizational information systems and information that are intended for public access (e.g., individuals accessing federal information through public interfaces to organizational information systems).

DHS-2.15.29.3 Requirement Enhancements:

- The organization shall establish terms and conditions for the use of external information systems in accordance with organizational security policies and procedures. The terms and conditions address, as a minimum the types of applications that can be accessed on the organizational information system from the external information system.

- The organization prohibits authorized individuals from using an external system to access the AMI system or to process, store, or transmit organization-controlled information except in situations where the organization: 1) can verify the employment of required security mechanisms on the external system as specified in the organization’s security policy and system security plan; or 2) has approved system connection or processing agreements with the organizational entity hosting the external system.

ASAP-2.15.30 Unauthorized Access Reporting

ASAP-2.15.30.1 Requirement:

The AMI components must record and report unauthorized and unsuccessful attempts to access the system.

ASAP-2.15.30.2 Supplemental Guidance

This can be accomplished with a number of approaches including:

- System Use Notification (DHS-2.15.17, DHS-2.15.19, DHS-2.15.20)

- Previous Logon Notification

- Unsuccessful Login Attempts

ASAP-2.15.30.3 Requirement Enhancements:

None.

ASAP-2.15.31 Unauthorized Access

ASAP-2.15.31.1 Requirement:

The AMI components limit opportunities for unauthorized access.

ASAP-2.15.31.2 Supplemental Guidance

This can be accomplished with a number of approaches including:

- Concurrent Session Control

- Session Lock

- Remote Session Termination

ASAP-2.15.31.3 Requirement Enhancements:

None.

2.16 Audit and Accountability

Periodic audits and logging of the AMI components and system need to be implemented to validate that the security mechanisms present during system validation testing are still installed and operating correctly. These security audits review and examine a system’s records and activities to determine the adequacy of system security controls and to ensure compliance with established security policy and procedures. Audits are also used to detect breaches in security services through examination of system logs. Logging is necessary for anomaly detection as well as forensic analysis.

DHS-2.16.1 Audit and Accountability Policy and Procedures

DHS-2.16.1.1 Requirement:

The organization shall develop, disseminate, and periodically review/update:

- A formal, documented, audit and accountability policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance;

- Formal, documented procedures to facilitate the implementation of the audit and accountability policy and associated audit and accountability controls.

DHS-2.16.1.2 Supplemental Guidance:

The organization shall ensure the audit and accountability policy and procedures are consistent with applicable federal laws, directives, policies, regulations, standards, and guidance. The audit and accountability policy can be included as part of the general security policy for the organization. Procedures can be developed for the security program in general, and for a particular AMI component, when required.

DHS-2.16.1.3 Requirement Enhancements:

None.

DHS-2.16.2 Auditable Events

DHS-2.16.2.1 Requirement:

All AMI components must generate audit records, at a minimum, for the following events whether or not the attempts were successful:

- Security Events

- Control Events

- System/Device Configuration Changes

All AMI systems and components must transmit all audit records and logs to a dedicated log management system. Audit record generation and processing must not degrade the operational performance of the AMI components or system.

DHS-2.16.2.2 Supplemental Guidance:

The organization shall specify which AMI system components carry out auditing activities and ensure that certain events are included or excluded from the set of auditable events based on specified attributes. Auditing activity can affect AMI system performance; therefore, the organization decides, based on a risk assessment, which events require auditing continually and which events require auditing in response to specific situations. The organization defines auditable events that are adequate to support after-the-fact investigations of security incidents.

The targeted security functionality must be able to generate an audit record of:

- Startup and shutdown of the audit functions;

- Successful and failed logins

- Failed authentications of signed or encrypted requests

- Change in access control or privilege

- Changes to security settings

- Creation, deletion, or modifications of users, password, tokens, and security keys

- Triggering of tamper sensors

The purpose of this requirement is to identify significant and relevant events to the security of the AMI system that needs to be audited. The organization specifies which AMI components carry out auditing activities. Audit records can be generated at various levels of abstraction, including at the packet level as information traverses the network. Selecting the right level of abstraction for audit record generation is a critical aspect of an audit capability and can facilitate the identification of root causes to problems.

The organization must maintain a centralized log management system for long term storage and log correlation. This system must:

- Provide the capability to compile audit records from multiple components throughout the system into a system wide (logical or physical), time-correlated audit trail.

- Provide the capability to manage the selection of events to be audited by individual components of the system.

- Provide the organization the ability to periodically review and update the list of organization-defined auditable events.

DHS-2.16.3 Content of Audit Records

DHS-2.16.3.1 Requirement:

All AMI components must capture sufficient and detailed information in audit records to establish what events occurred, the sources of the events, and their outcomes.

DHS-2.16.3.2 Supplemental Guidance:

Two types of audits must be tracked:

- General quality assurance audits of the configuration and operation of the AMI system that verify compliance with organization’s security plan;

- Audits of operational events encountered by the AMI system when the system operates outsides its normal operating parameters.

General quality assurance audit records contain information of what was audited and the results of the audit; that is, the system is in compliance or not, and if not, what areas are out of compliance. Operational event audits are initiated by the organization’s corrective action process when the AMI system operates outsides its normal operating parameters.

Audit record content typically includes:

- Date and time of the event;

- The component of the AMI system (e.g., software or hardware component) where the event occurred;

- Type of event;

- User/subject/device identity;

- The operational consequences in the case of an operational event.

All AMI components must provide the capability to include additional, more detailed information in the records for audit events identified by type, location, or subject. All AMI systems and components must provide the capability to centrally manage the content of audit records generated by individual components throughout the AMI system.

DHS-2.16.4 Audit Storage Capacity

DHS-2.16.4.1 Requirement:

All AMI components must provide sufficient audit record storage capacity and capabilities to configure auditing verbosity to reduce the likelihood of such capacity being exceeded.

Under normal usage conditions, components and systems must store events locally for the following minimal timeframes:

- Embedded Devices: 1 week

- Traditional IT or SCADA Servers: 1 month

- Central Log Management Systems: 1 year

DHS-2.16.4.2 Supplemental Guidance:

None.

DHS-2.16.4.3 Requirement Enhancements:

None.

DHS-2.16.5 Response to Audit Processing Failures

DHS-2.16.5.1 Requirement:

The log management system must alert appropriate organization personnel in case of audit failure events, such as:

- Allocated audit record storage volume reaches organization-defined percentage of maximum audit record storage capacity.

- Log management systems have not received log messages from a particular AMI component for a configurable period of time.

- Inability to read from or write to the event storage volume.

DHS-2.16.5.2 Supplemental Guidance:

Audit processing failures include, for example, software/hardware errors, failures in the audit capturing mechanisms, and audit storage capacity being reached or exceeded.

DHS-2.16.5.3 Requirement Enhancements:

- The AMI system provides a warning when allocated audit record storage volume reaches organization-defined percentage of maximum audit record storage capacity;

- The AMI system provides a real-time alert when the following organization defined audit failure events occur.

DHS-2.16.6 Audit Monitoring, Analysis, and Reporting

DHS-2.16.6.1 Requirement:

The organization regularly monitors, reviews, and analyzes audit records on all dedicated log management systems. The log management systems must provide automated mechanisms for detecting inappropriate, unusual, or suspicious activity or security violations, and automatically alerts appropriate personnel in a timely manner.

DHS-2.16.6.2 Supplemental Guidance:

Organizations increase the level of audit monitoring and analysis activity within the log management systems and audit record sources whenever there is an indication of increased risk to organizational operations, organizational assets, or individuals based on law enforcement information, intelligence information, or other credible sources of information. AMI components and system must support this ability. Audit records need to be monitored regularly for inappropriate activities in accordance with organizational procedures. Audit reports need to be provided to those responsible for cyber security.

DHS-2.16.6.3 Requirement Enhancements:

None.

DHS-2.16.7 Audit Reduction and Report Generation

DHS-2.16.7.1 Requirement:

The dedicated log management systems must provide an audit reduction and report generation capability.

DHS-2.16.7.2 Supplemental Guidance:

Audit reduction, review, and reporting tools support after-the-fact investigations of security incidents without altering original audit records.

DHS-2.16.7.3 Requirement Enhancements:

None.

DHS-2.16.8 Time Stamps

DHS-2.16.8.1 Requirement:

All AMI system and components must provide time stamps for use in audit record generation.

DHS-2.16.8.2 Supplemental Guidance:

Time stamps of audit records are generated using internal system clocks synchronized across all of the AMI components.

DHS-2.16.8.3 Requirement Enhancements:

None.

DHS-2.16.9 Protection of Audit Information

DHS-2.16.9.1 Requirement:

All AMI components and system must protect audit information and audit tools from unauthorized access, modification, and deletion.

DHS-2.16.9.2 Supplemental Guidance:

Audit information includes all information (e.g., audit records, audit settings, and audit reports) needed to successfully audit AMI system activity. The logs are important for error correction, security breach recovery, investigations, and related efforts.

DHS-2.16.9.3 Requirement Enhancements:

None.

DHS-2.16.10 Audit Record Retention

DHS-2.16.10.1 Requirement:

The organization shall retain audit logs for an organization-defined time period to provide support for after-the-fact investigations of security incidents and to meet regulatory and organizational information retention requirements.

DHS-2.16.10.2 Supplemental Guidance:

Logs containing computer or communication system security relevant events need to be retained for a period as defined in the information retention policy. The organization retains audit records until it is determined that they are no longer needed for administrative, legal, regulatory, or other operational purposes.

DHS-2.16.10.3 Requirement Enhancements:

None.

DHS-2.16.11 Conduct and Frequency of Audits

DHS-2.16.11.1 Requirement:

The organization shall conduct audits at planned intervals to determine whether the security objectives, measures, processes, and procedures:

- Conform to the requirements and relevant legislation or regulations;

- Conform to the identified information security requirements;

- Are effectively implemented and maintained;

- Perform as expected;

- Identify inappropriate activities.

DHS-2.16.11.2 Supplemental Guidance:

Audits can be either in the form of internal self-assessment or independent, third-party audits. Internal audits, sometimes called first-party audits, are conducted by, or on behalf of, the organization itself for internal purposes. An internal audit needs to be conducted to ensure that documentation is current with any changes to the AMI system. Independent audits review and examine records and activities to assess the adequacy of AMI system security measures, ensure compliance with established policies and operational procedures, and recommend necessary changes in security requirements, policies, or procedures. For independent audits, the auditor(s) need to be accompanied by an appropriate knowledgeable AMI system staff person(s) to answer any questions about the particular system under review.

DHS-2.16.11.3 Requirement Enhancements:

None.

DHS-2.16.12 Auditor Qualification

DHS-2.16.12.1 Requirement:

The organization’s audit program shall specify auditor qualifications in accordance with the organization’s documented training program.

DHS-2.16.12.2 Supplemental Guidance:

The selection of auditors and conduct of audits must ensure the objectivity and impartiality of the audit process. Security auditors need to:

- Understand the AMI system to be audited and be personally familiar with the systems and operating practices;

- Understand the risk involved with the audit and the consequences associated with unintentional stimulus or denial of service to the AMI system;

- Fully understand the corporate cyber and AMI system security policies and procedures and the specific health, safety, and environmental risks associated with a particular facility and/or process.

DHS-2.16.12.3 Requirement Enhancements:

The organization assigns auditor and system administration functions to separate personnel.

ASAP-2.16.13 Audit Tools

ASAP-2.16.13.1 Requirement:

The organization under the audit program shall specify strict rules and careful use of audit tools when auditing AMI system functions.

ASAP-2.16.13.2 Supplemental Guidance:

As a general practice, system audits determine compliance of the AMI system to the organization’s security plan. For new AMI components, system auditing utilities need to be incorporated into the design. Appropriate security audit practices for legacy systems require appropriate precautions be taken before assessing the AMI system. For AMI system audits to determine inappropriate activity, information custodians ensure that AMI system monitoring tools are installed to log system activity and security events. Auditing and log management tools need to be used cautiously in maintaining and proving the integrity of the AMI system from installation through the system life cycle. Access to AMI system audit tools need to be protected to prevent any possible misuse or compromise.

ASAP-2.16.13.3 Requirement Enhancements:

The AMI system and its components shall continue to operate during and after a cyber security scan.

DHS-2.16.14 Security Policy Compliance

DHS-2.16.14.1 Requirement:

The organization shall demonstrate compliance to the organization’s security policy through audits in accordance with the organization’s audit program.

DHS-2.16.14.2 Supplemental Guidance:

Periodic audits of the AMI system must be implemented to demonstrate compliance to the organization’s security policy. These audits:

- Assess whether the defined cyber security policies and procedures, including those to identify security incidents, are being implemented and followed;

- Document and ensure compliance to organization policies and procedures;

- Identify security concerns, validate the system is free from security compromises, and provide information on the nature and extent of compromises should they occur;

- Validate change management procedures and ensure that they produce an audit trail of reviews and approvals of all changes;

- Verify that security mechanisms and management practices present during system validation are still in place and functioning;

Ensure reliability and availability of the system to support safe operation;

Continuously improve performance.

DHS-2.16.14.3 Requirement Enhancements:

None.

# Footnotes

http://www.smartgridipedia.org/index.php/Use_Cases_with_Integration_Requirements

After this filter step, several actors were left "orphaned" in the diagram—interacting with no other actor or in-scope component. They—Customer, Customer Representative, DG Evaluation Team, and Third Party Organizations—were removed.

A listing of the raw material used to compile these summaries is found in Appendix A.

This probably shouldn't go from both AMI Management System and AMI Network Management System to Head End.

This component was labeled MDMS: AMI Management System in the source scenarios.

This component was labeled MDMS: AMI Network Management System in the source scenarios.

This component was labeled MDMS: Meter Data Unification System in the source scenarios.

THE INTEGRATED ENERGY AND COMMUNICATION SYSTEMS ARCHITECTURE, EPRI, Palo Alto, CA and Electricity Innovation Institute, Palo Alto, CA: 2003

AMI System Security Requirements v1.0 Revised, UCA International Users Group – AMI-SEC Task Force, Knoxville, TN: 2008

North American Electric Reliability Corporation. 2006, June 1. NERC Critical Infrastructure Protection (CIP). Retrieved from http://www.nerc.com/page.php?cid=2|20

Department of Homeland Security, National Cyber Security Division. 2008, January. Catalog of Control Systems Security: Recommendations for Standards Developers. Retrieved from http://www.us-cert.gov/control_systems/